## 1.DGMS Survey Summary
FORM No: | [5 empty] | REV. NO
Reference: DGMS(Tech) Circular No. 11 of 2016 Dated 27/06/2016 anf notification dated 28/04/2017
0
DATE OF SURVEY: |  | 2024-12-18 |  |  |  | AREA: | Mining
Lux Meter: | WISE by Bidaal
ILLUMINATION LEVEL SURVEY REPORT
Area Code | Place/Area to be illuminated |  | Minimum standards of illumination to be provided (in lux)
|  |  | H | Actual | V | Actual | Location | Remarks
1 | Work place of Heavy Machinery |  | 15 | 322.1061 | 25 | 22 | DUMPER 37 (PIT-1), E579 SHOVEL (PIT-1), E571 SHOVEL (PIT-1)
2.1 | Area where drilling rig works |  | NA | 51 | 25 | 49.9963 | DRILL 664 KH-1 PIT-2, ROC L8 KH-1 PIT-2
2.2 | Area where drill holes exists |  | 15 | 31.3363 | NA | NA | DRILL 664 KH-1 PIT-2 (HOLE), ROC L8 KH-1 PIT-2 (HOLE)
3 | Places where manual work is done |  | 15 | No Data | 25 | No data
4 | Places where loading, unloading or transfer,loading of dumpers,trucks or train is carried on (including OB Dump and Mineral/Ore stack Yard ) |  | 15 | 31.3724 | 15 | 23.5885 | HOPPER KH-1 SCREEN PLANT, SIZE ORE BC-3, S3 STOCK, S10 STOCK, S11 STOCK, S9 (LMV), S8, S4, S5
5 | Operator cabins of machines or mechanism |  | 50 | 326.661 | NA | NA | DRILL 664 KH-1 PIT-2 (CABIN), ROC L8 KH-1 PIT-2 (CABIN), E579 SHOVEL (PIT-1) (CABIN), E571 SHOVEL (PIT-1) (CABIN), SHOVEL E-571 PIT-1
6 | Haul roads for Trucks and Dumpers |  | 10 | 50.9646 | NA | NA | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK), HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN), HAUL ROAD (IM SECTION TO SUBGRADEDUMP), HAUL ROAD, HAUL ROAD (SUBGRADE TO 710RL), HAUL ROAD (IM SECTION TO PIT-1), HAUL ROAD (PIT-1 16D), HAUL ROAD (TLS TO PIT-11 VIEW), HAUL ROAD ( TWIN CANTEEN TO PCH), HAUL ROAD (TWIN CANTEEN TO METSO), HAUL ROAD (METSO TO KH-1 TRF ROOM), HAUL ROAD (PB GATE TO OLD EQUIPMENT), HAUL ROAD (OLD EQUIPMENT TO S3), HAUL ROAD (KH-1 IRC TO PB GATE), HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY), HAUL ROAD (TO GATE-1), HAUL ROAD (TO ADMIN), HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX)
7 | Rail haulage track in the pit |  | 10 | No Data | NA | NA
8 | Roadways and footpaths from bench to bench |  | 10 | No Data | NA | NA
9 | Permanent paths for use of persons employed |  | 10 | 89.8931 | NA | NA | DUMPER TERMINAL PARKING, MANGLA PARKING PATHWAY, DUMPER TERMINAL PATHWAY, OFFICE AREA PATHWAY
10 | In-pit Crusher/Feeder Breaker |  | 40 | No Data | NA | NA
11 | Hand picking points |  | 50 | No Data | NA | NA
Conveyers
12.1 | Transfer points and drive/tail end area |  | 40 | No Data | NA | NA
12.2 | Along Conveyor |  | 20 | 64.7633 | NA | NA | BC-1, BC-2, BC-4 (CONVEYOR)
Mineral/ Ore handling plant
13.1 | Places of crushing, screening, segregation and loading/Unloading |  | 40 | No Data | NA | NA
13.2 | Operation points |  | 50 | 126.9783 | NA | NA | KH-1 SCREEN PLANT
13.3 | Other places (in general) |  | 20 | 22.025 | NA | NA | DIESEL PUMP AREA
14 | Pumping stations |  | 40 | 27 | NA | NA | PUMP ROOM
15.1 | Electrical Sub-Stations |  | 100 | 443.0367 | 50 | 165.2208 | GARDEN SUBSTATION
15.2 | Other places of operation of electrical apparatus/equipment |  | 20 | 74.7127 | 20 | 32.275 | FEEDER (GARDEN SUBSTATION), MCC ROOM, UPS ROOM
16 | First Aid station |  | 50 | 69.5497 | NA | NA | FIRST AID STATION
17 | Rest shelter |  | 30 | 70.716 | NA | NA | REST SHELTER
18 | Workshop |  | 100 | 144.1036 | 50 | 55.2227 | WORKSHOP (NEAR EQUIPMENT OFFICE)
19 | Parking Yard |  | 50 | 30 | NA | NA | TDV PARKING, MANGLA PARKING
20 | General working area |  | 10 | 85.165 | NA | NA | MANGLA CABIN, STORE AREA
REMARKS:
| Shift In-charge |  | Manager |  |  |  | Mine Manager

## 2.Location-wise Summary
SN | Locations | Area Code | H_req | H_actual | V_req | V_actual | Remarks | SN | Place/Area to be illuminated | Locations | Area Code | H_req | H_actual | V_req | V_actual
1 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 6 | 10 | 120.6751 | NA | 15.7951 |  | 1 | Work place of Heavy Machinery | [6 empty] | 1 | Poor | less than 50% of required lux
2 | REST SHELTER | 17 | 30 | 70.716 | NA | 59.7383 |  |  |  | DUMPER 37 (PIT-1) | 1 | 15 | 49.76 | 25 | 51.58 |  | Moderate | between 50% & 75% o required lux
3 | TDV PARKING | 19 | 50 | 30 | NA | 66.8405 |  |  |  | E579 SHOVEL (PIT-1) | 1 | 15 | 17.2906 | 25 | 37.3945 |  | Good | more than 75% of required lux
4 | DUMPER TERMINAL PARKING | 9 | 10 | 44.8883 | NA | 74.8941 |  |  |  | E571 SHOVEL (PIT-1) | 1 | 15 | 512.9123 | 25 | 12
5 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 6 | 10 | 47.6003 | NA | 16.1536 |  | 2 | Area where drilling rig works | [6 empty] | 2.1
6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 6 | 10 | 13.8358 | NA | 6 |  |  |  | DRILL 664 KH-1 PIT-2 | 2.1 | NA | 42 | 25 | 49
7 | HAUL ROAD | 6 | 10 | 21.5109 | NA | 15.27 |  |  |  | ROC L8 KH-1 PIT-2 | 2.1 | NA | 63 | 25 | 53
8 | HAUL ROAD (SUBGRADE TO 710RL) | 6 | 10 | 18.888 | NA | 3 |  | 3 | Area where drill holes exists | [6 empty] | 2.2
9 | DRILL 664 KH-1 PIT-2 | 2.1 | NA | 42 | 25 | 49 |  |  |  | DRILL 664 KH-1 PIT-2 (HOLE) | 2.2 | 15 | 46.434 | NA | 3
10 | DRILL 664 KH-1 PIT-2 (HOLE) | 2.2 | 15 | 46.434 | NA | 3 |  |  |  | ROC L8 KH-1 PIT-2 (HOLE) | 2.2 | 15 | 7 | NA | 11
11 | DRILL 664 KH-1 PIT-2 (CABIN) | 5 | 50 | 286.195 | NA | 228.495 |  | 4 | Places where loading, unloading or transfer, loading of dumpers, trucks or train is carried on (including OB Dump and Mineral/Ore stack Yard) | [6 empty] | 4
12 | ROC L8 KH-1 PIT-2 | 2.1 | NA | 63 | 25 | 53 |  |  |  | HOPPER KH-1 SCREEN PLANT | 4 | 15 | 21.4841 | 15 | 30.8827
13 | ROC L8 KH-1 PIT-2 (CABIN) | 5 | 50 | 371.2978 | NA | 94.4867 |  |  |  | SIZE ORE BC-3 | 4 | 15 | 17.4289 | 15 | 30.1733
14 | ROC L8 KH-1 PIT-2 (HOLE) | 2.2 | 15 | 7 | NA | 11 |  |  |  | S3 STOCK | 4 | 15 | 119.56 | 15 | 27.524
15 | HAUL ROAD (IM SECTION TO PIT-1) | 6 | 10 | 15.6435 | NA | 8 |  |  |  | S10 STOCK | 4 | 15 | 35.585 | 15 | 5
16 | DUMPER 37 (PIT-1) | 1 | 15 | 49.76 | 25 | 51.58 |  |  |  | S11 STOCK | 4 | 15 | 24.18 | 15 | 12
17 | E579 SHOVEL (PIT-1) | 1 | 15 | 17.2906 | 25 | 37.3945 |  |  |  | S9 (LMV) | 4 | 15 | 22.6375 | 15 | 24.7538
18 | E579 SHOVEL (PIT-1) (CABIN) | 5 | 50 | 224.7425 | NA | 8 |  |  |  | S8 | 4 | 15 | 13 | 15 | 7
19 | E571 SHOVEL (PIT-1) (CABIN) | 5 | 50 | 682.265 | NA | 7 |  |  |  | S4 | 4 | 15 | 36.9967 | 15 | 46.7233
20 | E571 SHOVEL (PIT-1) | 1 | 15 | 512.9123 | 25 | 12 |  |  |  | S5 | 4 | 15 | 86.5175 | 15 | 59.725
21 | SHOVEL E-571 PIT-1 | 5 | 50 | 251.51 | NA | 43 |  | 5 | Operator cabins of machines or mechanism | [6 empty] | 5
22 | HAUL ROAD (PIT-1 16D) | 6 | 10 | 8 | NA | 6 |  |  |  | DRILL 664 KH-1 PIT-2 (CABIN) | 5 | 50 | 286.195 | NA | 228.495
23 | HAUL ROAD (TLS TO PIT-11 VIEW) | 6 | 10 | 21.3305 | NA | 10.1773 |  |  |  | ROC L8 KH-1 PIT-2 (CABIN) | 5 | 50 | 371.2978 | NA | 94.4867
24 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 6 | 10 | 36.1573 | NA | 16.9845 |  |  |  | E579 SHOVEL (PIT-1) (CABIN) | 5 | 50 | 224.7425 | NA | 8
25 | HAUL ROAD (TWIN CANTEEN TO METSO) | 6 | 10 | 21.1871 | NA | 9 |  |  |  | E571 SHOVEL (PIT-1) (CABIN) | 5 | 50 | 682.265 | NA | 7
26 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 6 | 10 | 12.9619 | NA | 7 |  |  |  | SHOVEL E-571 PIT-1 | 5 | 50 | 251.51 | NA | 43
27 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 6 | 10 | 44.903 | NA | 24.9528 |  | 6 | Haul roads for Trucks and Dumpers | [6 empty] | 6
28 | MANGLA PARKING | 19 | 50 | 19 | NA | 21 |  |  |  | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 6 | 10 | 120.6751 | NA | 15.7951
29 | MANGLA PARKING PATHWAY | 9 | 10 | 68.2277 | NA | 26.0691 |  |  |  | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 6 | 10 | 47.6003 | NA | 16.1536
30 | HAUL ROAD (OLD EQUIPMENT TO S3) | 6 | 10 | 3 | NA | 11.9036 |  |  |  | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 6 | 10 | 13.8358 | NA | 6
31 | HOPPER KH-1 SCREEN PLANT | 4 | 15 | 21.4841 | 15 | 30.8827 |  |  |  | HAUL ROAD | 6 | 10 | 21.5109 | NA | 15.27
32 | MANGLA CABIN | 20 | 10 | 90.6175 | NA | 153.3975 |  |  |  | HAUL ROAD (SUBGRADE TO 710RL) | 6 | 10 | 18.888 | NA | 3
33 | KH-1 SCREEN PLANT | 13.2 | 50 | 126.9783 | NA | 103.1167 |  |  |  | HAUL ROAD (IM SECTION TO PIT-1) | 6 | 10 | 15.6435 | NA | 8
34 | BC-1, BC-2, BC-4 (CONVEYOR) | 12.2 | 20 | 64.7633 | NA | 46.6494 |  |  |  | HAUL ROAD (PIT-1 16D) | 6 | 10 | 8 | NA | 6
35 | SIZE ORE BC-3 | 4 | 15 | 17.4289 | 15 | 30.1733 |  |  |  | HAUL ROAD (TLS TO PIT-11 VIEW) | 6 | 10 | 21.3305 | NA | 10.1773
36 | HAUL ROAD (KH-1 IRC TO PB GATE) | 6 | 10 | 14.3789 | NA | 4 |  |  |  | HAUL ROAD ( TWIN CANTEEN TO PCH) | 6 | 10 | 36.1573 | NA | 16.9845
37 | S3 STOCK | 4 | 15 | 119.56 | 15 | 27.524 |  |  |  | HAUL ROAD (TWIN CANTEEN TO METSO) | 6 | 10 | 21.1871 | NA | 9
38 | GARDEN SUBSTATION | 15.1 | 100 | 443.0367 | 50 | 165.2208 |  |  |  | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 6 | 10 | 12.9619 | NA | 7
39 | FEEDER (GARDEN SUBSTATION) | 15.2 | 20 | 33.596 | 20 | 28.16 |  |  |  | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 6 | 10 | 44.903 | NA | 24.9528
40 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 6 | 10 | 7 | NA | 3 |  |  |  | HAUL ROAD (OLD EQUIPMENT TO S3) | 6 | 10 | 3 | NA | 11.9036
41 | S10 STOCK | 4 | 15 | 35.585 | 15 | 5 |  |  |  | HAUL ROAD (KH-1 IRC TO PB GATE) | 6 | 10 | 14.3789 | NA | 4
42 | S11 STOCK | 4 | 15 | 24.18 | 15 | 12 |  |  |  | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 6 | 10 | 7 | NA | 3
43 | S9 (LMV) | 4 | 15 | 22.6375 | 15 | 24.7538 |  |  |  | HAUL ROAD (TO GATE-1) | 6 | 10 | 23.7954 | NA | 5
44 | HAUL ROAD (TO GATE-1) | 6 | 10 | 23.7954 | NA | 5 |  |  |  | HAUL ROAD (TO ADMIN) | 6 | 10 | 20.3747 | NA | 6
45 | S8 | 4 | 15 | 13 | 15 | 7 |  |  |  | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 6 | 10 | 46.2631 | NA | 17.2604
46 | HAUL ROAD (TO ADMIN) | 6 | 10 | 20.3747 | NA | 6 |  | 7 | Permanent paths for use of persons employed | [6 empty] | 9
47 | S4 | 4 | 15 | 36.9967 | 15 | 46.7233 |  |  |  | DUMPER TERMINAL PARKING | 9 | 10 | 44.8883 | NA | 74.8941
48 | S5 | 4 | 15 | 86.5175 | 15 | 59.725 |  |  |  | MANGLA PARKING PATHWAY | 9 | 10 | 68.2277 | NA | 26.0691
49 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 6 | 10 | 46.2631 | NA | 17.2604 |  |  |  | DUMPER TERMINAL PATHWAY | 9 | 10 | 113.3294 | NA | 39.3506
50 | DUMPER TERMINAL PATHWAY | 9 | 10 | 113.3294 | NA | 39.3506 |  |  |  | OFFICE AREA PATHWAY | 9 | 10 | 83.8348 | NA | 25.7074
51 | FIRST AID STATION | 16 | 50 | 69.5497 | NA | 34 |  | 8 | Along Conveyor | [6 empty] | 12.2
52 | DIESEL PUMP AREA | 13.3 | 20 | 22.025 | NA | 30.1621 |  |  |  | BC-1, BC-2, BC-4 (CONVEYOR) | 12.2 | 20 | 64.7633 | NA | 46.6494
53 | STORE AREA | 20 | 10 | 74.26 | NA | 109.74 |  | 9 | Operation points | [6 empty] | 13.2
54 | MCC ROOM | 15.2 | 20 | 97.1422 | 20 | 46.9533 |  |  |  | KH-1 SCREEN PLANT | 13.2 | 50 | 126.9783 | NA | 103.1167
55 | OFFICE AREA PATHWAY | 9 | 10 | 83.8348 | NA | 25.7074 |  | 10 | Other places (in general) | [6 empty] | 13.3
56 | PUMP ROOM | 14 | 40 | 27 | NA | 20 |  |  |  | DIESEL PUMP AREA | 13.3 | 20 | 22.025 | NA | 30.1621
57 | UPS ROOM | 15.2 | 20 | 75.0225 | 20 | 22.9808 |  | 11 | Pumping stations | [6 empty] | 14
58 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 18 | 100 | 144.1036 | 50 | 56 |  |  |  | PUMP ROOM | 14 | 40 | 27 | NA | 20
[8 empty] | 12 | Electrical Sub-Stations | [6 empty] | 15.1
[10 empty] | GARDEN SUBSTATION | 15.1 | 100 | 443.0367 | 50 | 165.2208
[8 empty] | 13 | Other places of operation of electrical apparatus/equipment | [6 empty] | 15.2
[10 empty] | FEEDER (GARDEN SUBSTATION) | 15.2 | 20 | 33.596 | 20 | 28.16
[10 empty] | MCC ROOM | 15.2 | 20 | 97.1422 | 20 | 46.9533
[10 empty] | UPS ROOM | 15.2 | 20 | 75.0225 | 20 | 22.9808
[8 empty] | 14 | First Aid station | [6 empty] | 16
[10 empty] | FIRST AID STATION | 16 | 50 | 69.5497 | NA | 34
[8 empty] | 15 | Rest shelter | [6 empty] | 17
[10 empty] | REST SHELTER | 17 | 30 | 70.716 | NA | 59.7383
[8 empty] | 16 | Workshop | [6 empty] | 18
[10 empty] | WORKSHOP (NEAR EQUIPMENT OFFICE) | 18 | 100 | 144.1036 | 50 | 56
[8 empty] | 17 | Parking Yard | [6 empty] | 19
[10 empty] | TDV PARKING | 19 | 50 | 30 | NA | 66.8405
[10 empty] | MANGLA PARKING | 19 | 50 | 19 | NA | 21
[8 empty] | 18 | General working area | [6 empty] | 20
[10 empty] | MANGLA CABIN | 20 | 10 | 90.6175 | NA | 153.3975
[10 empty] | STORE AREA | 20 | 10 | 74.26 | NA | 109.74
0
0

## Detailed Analysis
date | time | latitude | longitude | horizontal lux | vertical lux | Area/Place Code | Location | Distance | Serial |  |  | Area | count | H_Avg_90 | V_Avg_90 | H_Avg_10 | V_Avg_10 | Mean_H | Mean_V | Median_H | Median_V | Mode_H | Mode_V | variance.P_H | variance.P_V | max_H | max_H_count | max_V | Max_V_count | min_H | min_H_count | min_H_%count | H_Avg_50 | V_Avg_50
2024-12-18 | 18:35 | 21.9419 | 85.3874 | 12.8 | 26.31 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) |  | 1 |  |  | 1 | 93 | 322.1061 | 21.9714 | 0 | 0 | 322.1061 | 21.9714 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 14 | 0 | 10 | 0 | 14 | 15.05% | 322.1061 | 21.9714
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 63.36 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 2 | Mine Name |  | 2.1 | 145 | 50.6694 | 49.9963 | 0 | 0 | 50.6694 | 49.9963 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 17 | 0 | 42 | 0 | 17 | 11.72% | 50.6694 | 49.9963
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 93.32 | 221.88 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 3 | Date | 2024-12-18 | 2.2 | 8 | 31.3363 | 5.555 | #DIV/0! | 0 | 31.3363 | 5.555 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0% | 31.3363 | 5.555
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 87.87 | 216.39 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 4 | Count | 5878 | 3 | 0 | No Data | No Data | No Data | No Data | No Data | No Data | NA | NA | NA | NA | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No data
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 79.7 | 208.16 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 5 | Distance(Km) | 43.2574 | 4 | 79 | 31.3724 | 23.5885 | 0 | 0 | 31.3724 | 23.5885 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 1 | 0 | 15 | 0 | 1 | 1.266% | 31.3724 | 23.5885
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 26.31 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 6 |  |  | 5 | 29 | 326.661 | 115.3638 | #DIV/0! | 0 | 326.661 | 115.3638 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0% | 326.661 | 115.3638
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 147.92 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 7 |  |  | 6 | 5085 | 155.1288 | 83.4891 | 0 | 0 | 24.8172 | 12.8815 | 7.58 | 5.24 | 0 | 5.24 | 6594.2184 | 1398.2075 | 1026.08 | 0 | 526.22 | 0 | 0 | 1944 | 38.23% | 50.9646 | 27.3601
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 142.45 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 8 |  |  | 7 | 0 | No Data | No Data | No Data | No Data | No Data | No Data | NA | NA | NA | NA | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No data
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 131.52 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 9 |  |  | 8 | 0 | No Data | No Data | No Data | No Data | No Data | No Data | NA | NA | NA | NA | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No data
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 106.96 | 10.12 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 10 |  |  | 9 | 67 | 89.8931 | 30.1316 | #DIV/0! | 0 | 89.8931 | 30.1316 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0% | 89.8931 | 30.1316
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 115.14 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 11 |  |  | 10 | 0 | No Data | No Data | No Data | No Data | No Data | No Data | NA | NA | NA | NA | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No data
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 23.79 | 18.36 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 12 |  |  | 11 | 0 | No Data | No Data | No Data | No Data | No Data | No Data | NA | NA | NA | NA | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No data
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 136.99 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 13 |  |  | 12.1 | 0 | No Data | No Data | No Data | No Data | No Data | No Data | NA | NA | NA | NA | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No data
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 126.06 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 14 |  |  | 12.2 | 18 | 64.7633 | 46.6494 | #DIV/0! | #DIV/0! | 64.7633 | 46.6494 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 64.7633 | 46.6494
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 128.79 | 3.16 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 15 |  |  | 13.1 | 0 | No Data | No Data | No Data | No Data | No Data | No Data | NA | NA | NA | NA | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No Data | No data
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 134.25 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 16 |  |  | 13.2 | 6 | 126.9783 | 103.1167 | #DIV/0! | #DIV/0! | 126.9783 | 103.1167 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 126.9783 | 103.1167
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 131.52 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 17 |  |  | 13.3 | 14 | 22.025 | 30.1621 | 0 | 0 | 22.025 | 30.1621 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 2 | 0 | 3 | 0 | 2 | 14.29% | 22.025 | 30.1621
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 126.06 | 3.16 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 18 |  |  | 14 | 4 | 26.1575 | 19.67 | #DIV/0! | #DIV/0! | 26.1575 | 19.67 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 26.1575 | 19.67
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 126.06 | 10.12 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 19 |  |  | 15.1 | 36 | 443.0367 | 165.2208 | #DIV/0! | 0 | 443.0367 | 165.2208 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0% | 443.0367 | 165.2208
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 128.79 | 3.16 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 20 |  |  | 15.2 | 26 | 74.7127 | 32.275 | #DIV/0! | 0 | 74.7127 | 32.275 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0% | 74.7127 | 32.275
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 126.06 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 21 |  |  | 16 | 29 | 69.5497 | 33.6624 | 0 | 0 | 69.5497 | 33.6624 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 4 | 0 | 6 | 0 | 4 | 13.79% | 69.5497 | 33.6624
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 126.06 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 22 |  |  | 17 | 72 | 70.716 | 59.7383 | 0 | 0 | 70.716 | 59.7383 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 0 | 3 | 4.167% | 70.716 | 59.7383
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 128.79 | 3.16 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 23 |  |  | 18 | 73 | 144.1036 | 55.2227 | #DIV/0! | #DIV/0! | 144.1036 | 55.2227 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 144.1036 | 55.2227
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 126.06 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 24 |  |  | 19 | 88 | 29.4484 | 59.2633 | #DIV/0! | #DIV/0! | 29.4484 | 59.2633 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 29.4484 | 59.2633
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 131.52 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 25 |  |  | 20 | 6 | 85.165 | 138.845 | #DIV/0! | #DIV/0! | 85.165 | 138.845 | 0 | 0 | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 85.165 | 138.845
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 126.06 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 26
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 126.06 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 27
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 134.25 | 3.16 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 28 |  |  | Name of Location | Area Code | count | H_Avg_90 | V_Avg_90 | H_Avg_10 | V_Avg_10 | Mean_H | Mean_V | Median_H | Median_V | Mode_H | Mode_V | variance.P_H | variance.P_V | max_H | max_H_count | max_V | Max_V_count | min_H | min_H_count | min_H_%count | H_Avg_50 | V_Avg_50
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 134.25 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 29 |  |  | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 6 | 131 | 132.812 | 152.59 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 120.6751 | 15.7951
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 128.79 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 30 |  |  | REST SHELTER | 17 | 72 | 70.716 | 59.7383 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 70.716 | 59.7383
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 131.52 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 31 |  |  | TDV PARKING | 19 | 21 | 29.7629 | 66.8405 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 29.7629 | 66.8405
2024-12-18 | 18:36 | 21.9419 | 85.3874 | 128.79 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 32 |  |  | DUMPER TERMINAL PARKING | 9 | 46 | 44.8883 | 74.8941 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 44.8883 | 74.8941
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 128.79 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 33 |  |  | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 6 | 117 | 47.6003 | 16.1536 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 47.6003 | 16.1536
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 131.52 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 34 |  |  | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 6 | 60 | 13.8358 | 5.62 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 13.8358 | 5.62
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 35 |  |  | HAUL ROAD | 6 | 2930 | 21.5109 | 15.27 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 21.5109 | 15.27
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 128.79 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 36 |  |  | HAUL ROAD (SUBGRADE TO 710RL) | 6 | 64 | 18.888 | 2.453 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 18.888 | 2.453
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 128.79 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 37 |  |  | DRILL 664 KH-1 PIT-2 | 2.1 | 82 | 41.2968 | 48.042 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 41.2968 | 48.042
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 128.79 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 38 |  |  | DRILL 664 KH-1 PIT-2 (HOLE) | 2.2 | 5 | 46.434 | 2.652 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 46.434 | 2.652
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 128.79 | 10.12 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 39 |  |  | DRILL 664 KH-1 PIT-2 (CABIN) | 5 | 10 | 286.195 | 228.495 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 286.195 | 228.495
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 126.06 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 40 |  |  | ROC L8 KH-1 PIT-2 | 2.1 | 63 | 62.8686 | 52.54 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 62.8686 | 52.54
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 139.72 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 41 |  |  | ROC L8 KH-1 PIT-2 (CABIN) | 5 | 9 | 371.2978 | 94.4867 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 371.2978 | 94.4867
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 42 |  |  | ROC L8 KH-1 PIT-2 (HOLE) | 2.2 | 3 | 6.1733 | 10.3933 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 6.1733 | 10.3933
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 139.72 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 43 |  |  | HAUL ROAD (IM SECTION TO PIT-1) | 6 | 207 | 15.6435 | 7.133 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 15.6435 | 7.133
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 44 |  |  | DUMPER 37 (PIT-1) | 1 | 3 | 49.76 | 51.58 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 49.76 | 51.58
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 45 |  |  | E579 SHOVEL (PIT-1) | 1 | 33 | 17.2906 | 37.3945 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 17.2906 | 37.3945
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 46 |  |  | E579 SHOVEL (PIT-1) (CABIN) | 5 | 4 | 224.7425 | 7.12 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 224.7425 | 7.12
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 47 |  |  | E571 SHOVEL (PIT-1) (CABIN) | 5 | 2 | 682.265 | 6.41 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 682.265 | 6.41
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 131.52 | 3.16 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 48 |  |  | E571 SHOVEL (PIT-1) | 1 | 57 | 512.9123 | 11.4839 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 512.9123 | 11.4839
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 131.52 | 10.12 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 49 |  |  | SHOVEL E-571 PIT-1 | 5 | 4 | 251.51 | 42.23 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 251.51 | 42.23
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 134.25 | 10.12 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 50 |  |  | HAUL ROAD (PIT-1 16D) | 6 | 249 | 7.9718 | 5.8176 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 7.9718 | 5.8176
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 51 |  |  | HAUL ROAD (TLS TO PIT-11 VIEW) | 6 | 150 | 21.3305 | 10.1773 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 21.3305 | 10.1773
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 52 |  |  | HAUL ROAD ( TWIN CANTEEN TO PCH) | 6 | 120 | 36.1573 | 16.9845 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 36.1573 | 16.9845
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 136.99 | 10.12 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 53 |  |  | HAUL ROAD (TWIN CANTEEN TO METSO) | 6 | 90 | 21.1871 | 8.0854 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 21.1871 | 8.0854
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 54 |  |  | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 6 | 117 | 12.9619 | 6.6089 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 12.9619 | 6.6089
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 55 |  |  | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 6 | 53 | 44.903 | 24.9528 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 44.903 | 24.9528
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 136.99 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 56 |  |  | MANGLA PARKING | 19 | 25 | 18.2112 | 20.4844 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 18.2112 | 20.4844
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 57 |  |  | MANGLA PARKING PATHWAY | 9 | 22 | 68.2277 | 26.0691 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 68.2277 | 26.0691
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 58 |  |  | HAUL ROAD (OLD EQUIPMENT TO S3) | 6 | 11 | 2.0673 | 11.9036 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 2.0673 | 11.9036
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 136.99 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 59 |  |  | HOPPER KH-1 SCREEN PLANT | 4 | 22 | 21.4841 | 30.8827 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 21.4841 | 30.8827
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 136.99 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 60 |  |  | MANGLA CABIN | 20 | 4 | 90.6175 | 153.3975 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 90.6175 | 153.3975
2024-12-18 | 18:37 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 61 |  |  | KH-1 SCREEN PLANT | 13.2 | 6 | 126.9783 | 103.1167 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 126.9783 | 103.1167
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 136.99 | 3.16 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 62 |  |  | BC-1, BC-2, BC-4 (CONVEYOR) | 12.2 | 18 | 64.7633 | 46.6494 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 64.7633 | 46.6494
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 131.52 | 3.16 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 63 |  |  | SIZE ORE BC-3 | 4 | 9 | 17.4289 | 30.1733 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 17.4289 | 30.1733
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 136.99 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 64 |  |  | HAUL ROAD (KH-1 IRC TO PB GATE) | 6 | 141 | 14.3789 | 3.1617 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 14.3789 | 3.1617
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 3.16 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 65 |  |  | S3 STOCK | 4 | 5 | 119.56 | 27.524 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 119.56 | 27.524
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 3.16 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 66 |  |  | GARDEN SUBSTATION | 15.1 | 36 | 443.0367 | 165.2208 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 443.0367 | 165.2208
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 136.99 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 67 |  |  | FEEDER (GARDEN SUBSTATION) | 15.2 | 5 | 33.596 | 28.16 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 33.596 | 28.16
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 68 |  |  | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 6 | 140 | 6.6339 | 2.655 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 6.6339 | 2.655
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 69 |  |  | S10 STOCK | 4 | 8 | 35.585 | 4.155 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 35.585 | 4.155
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 70 |  |  | S11 STOCK | 4 | 7 | 24.18 | 11.8586 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 24.18 | 11.8586
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 136.99 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 71 |  |  | S9 (LMV) | 4 | 8 | 22.6375 | 24.7538 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 22.6375 | 24.7538
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 72 |  |  | HAUL ROAD (TO GATE-1) | 6 | 112 | 23.7954 | 4.5222 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 23.7954 | 4.5222
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 73 |  |  | S8 | 4 | 13 | 12.2315 | 6.2723 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 12.2315 | 6.2723
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 74 |  |  | HAUL ROAD (TO ADMIN) | 6 | 93 | 20.3747 | 5.2456 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 20.3747 | 5.2456
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 136.99 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 75 |  |  | S4 | 4 | 3 | 36.9967 | 46.7233 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 36.9967 | 46.7233
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 76 |  |  | S5 | 4 | 4 | 86.5175 | 59.725 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 86.5175 | 59.725
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 77 |  |  | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 6 | 300 | 46.2631 | 17.2604 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 46.2631 | 17.2604
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 78 |  |  | DUMPER TERMINAL PATHWAY | 9 | 18 | 113.3294 | 39.3506 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 113.3294 | 39.3506
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 79 |  |  | FIRST AID STATION | 16 | 29 | 69.5497 | 33.6624 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 69.5497 | 33.6624
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 80 |  |  | DIESEL PUMP AREA | 13.3 | 14 | 22.025 | 30.1621 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 22.025 | 30.1621
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 81 |  |  | STORE AREA | 20 | 2 | 74.26 | 109.74 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 74.26 | 109.74
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 131.52 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 82 |  |  | MCC ROOM | 15.2 | 9 | 97.1422 | 46.9533 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 97.1422 | 46.9533
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 128.79 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 83 |  |  | OFFICE AREA PATHWAY | 9 | 23 | 83.8348 | 25.7074 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 83.8348 | 25.7074
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 84 |  |  | PUMP ROOM | 14 | 4 | 26.1575 | 19.67 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 26.1575 | 19.67
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 128.79 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 85 |  |  | UPS ROOM | 15.2 | 12 | 75.0225 | 22.9808 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 75.0225 | 22.9808
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 10.12 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 86 |  |  | WORKSHOP (NEAR EQUIPMENT OFFICE) | 18 | 73 | 144.1036 | 55.2227 | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | #NA | 144.1036 | 55.2227
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 87
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 88
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 89
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 90
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 134.25 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 91
2024-12-18 | 18:38 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 92
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 93
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 94
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 134.25 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 95
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 96
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 97
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 128.79 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 98
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 128.79 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 99
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 131.52 | 10.12 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 100
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 101
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 128.79 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 102
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 128.79 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 103
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 104
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 105
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 106
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 107
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 108
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 109
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 134.25 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 110
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 111
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 112
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 134.25 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 113
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 131.52 | 7.58 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 114
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 106.96 | 10.12 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 115
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 79.7 | 10.12 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 116
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 76.97 | 10.12 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 117
2024-12-18 | 18:39 | 21.9419 | 85.3874 | 79.7 | 10.12 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 118
2024-12-18 | 18:39 | 21.9419 | 85.3873 | 33.45 | 10.12 | 17 | REST SHELTER | 10.3144 | 119
2024-12-18 | 18:39 | 21.9418 | 85.3873 | 5.24 | 10.12 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 11.1196 | 120
2024-12-18 | 18:39 | 21.9418 | 85.3873 | 15.57 | 26.31 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0 | 121
2024-12-18 | 18:40 | 21.9417 | 85.3872 | 26.31 | 36.16 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 15.1665 | 122
2024-12-18 | 18:40 | 21.9417 | 85.3872 | 38.88 | 15.57 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0.094935 | 123
2024-12-18 | 18:40 | 21.9416 | 85.3872 | 38.88 | 36.16 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 11.1196 | 124
2024-12-18 | 18:40 | 21.9415 | 85.3872 | 44.32 | 38.88 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 11.1192 | 125
2024-12-18 | 18:40 | 21.9414 | 85.3872 | 49.76 | 36.16 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 11.1192 | 126
2024-12-18 | 18:40 | 21.9414 | 85.3872 | 85.14 | 123.33 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 0 | 127
2024-12-18 | 18:40 | 21.9413 | 85.3872 | 5.24 | 18.36 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 11.1196 | 128
2024-12-18 | 18:40 | 21.9412 | 85.3872 | 10.12 | 5.24 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 11.1192 | 129
2024-12-18 | 18:40 | 21.9411 | 85.3872 | 10.12 | 10.12 | 19 | TDV PARKING | 11.1196 | 130
2024-12-18 | 18:40 | 21.941 | 85.3872 | 76.97 | 60.64 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 11.1192 | 131
2024-12-18 | 18:40 | 21.9409 | 85.3871 | 112.41 | 36.16 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 15.1668 | 132
2024-12-18 | 18:40 | 21.9409 | 85.387 | 199.93 | 85.14 | 6 | HAUL ROAD (GEM COMPLEX TO HAATHI CHOWK) | 10.3144 | 133
2024-12-18 | 18:40 | 21.9408 | 85.3869 | 79.7 | 23.79 | 9 | DUMPER TERMINAL PARKING | 15.1665 | 134
2024-12-18 | 18:40 | 21.9407 | 85.3868 | 221.88 | 7.58 | 9 | DUMPER TERMINAL PARKING | 15.1665 | 135
2024-12-18 | 18:40 | 21.9406 | 85.3867 | 134.25 | 104.23 | 9 | DUMPER TERMINAL PARKING | 15.1665 | 136
2024-12-18 | 18:40 | 21.9406 | 85.3867 | 117.87 | 10.12 | 9 | DUMPER TERMINAL PARKING | 0 | 137
2024-12-18 | 18:40 | 21.9405 | 85.3866 | 188.97 | 23.79 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 138
2024-12-18 | 18:40 | 21.9404 | 85.3865 | 87.87 | 71.53 | 19 | TDV PARKING | 15.1668 | 139
2024-12-18 | 18:40 | 21.9403 | 85.3864 | 123.33 | 7.58 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 140
2024-12-18 | 18:40 | 21.9403 | 85.3862 | 205.42 | 44.32 | 19 | DUMPER TERMINAL PARKING | 20.6283 | 141
2024-12-18 | 18:40 | 21.9402 | 85.3861 | 90.59 | 93.32 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 142
2024-12-18 | 18:40 | 21.9402 | 85.386 | 172.54 | 36.16 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3139 | 143
2024-12-18 | 18:40 | 21.9401 | 85.3859 | 183.49 | 44.32 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 144
2024-12-18 | 18:40 | 21.9401 | 85.3858 | 175.28 | 82.42 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3144 | 145
2024-12-18 | 18:40 | 21.94 | 85.3857 | 126.06 | 74.25 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 146
2024-12-18 | 18:40 | 21.94 | 85.3857 | 254.84 | 5.24 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 147
2024-12-18 | 18:40 | 21.9399 | 85.3856 | 101.5 | 68.8 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 148
2024-12-18 | 18:40 | 21.9399 | 85.3855 | 221.88 | 7.58 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3144 | 149
2024-12-18 | 18:40 | 21.9398 | 85.3854 | 93.32 | 71.53 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 150
2024-12-18 | 18:40 | 21.9397 | 85.3853 | 191.71 | 3.16 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 151
2024-12-18 | 18:40 | 21.9397 | 85.3853 | 126.06 | 98.77 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0.094935 | 152
2024-12-18 | 18:41 | 21.9396 | 85.3852 | 128.79 | 10.12 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 153
2024-12-18 | 18:41 | 21.9395 | 85.3851 | 219.14 | 49.76 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 154
2024-12-18 | 18:41 | 21.9394 | 85.385 | 63.36 | 7.58 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1671 | 155
2024-12-18 | 18:41 | 21.9394 | 85.3849 | 202.68 | 60.64 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3144 | 156
2024-12-18 | 18:41 | 21.9393 | 85.3848 | 188.97 | 85.14 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 157
2024-12-18 | 18:41 | 21.9393 | 85.3847 | 150.65 | 112.41 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3144 | 158
2024-12-18 | 18:41 | 21.9393 | 85.3846 | 213.65 | 5.24 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3144 | 159
2024-12-18 | 18:41 | 21.9394 | 85.3845 | 79.7 | 109.68 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 160
2024-12-18 | 18:41 | 21.9394 | 85.3843 | 186.23 | 3.16 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 20.6287 | 161
2024-12-18 | 18:41 | 21.9394 | 85.3842 | 3.16 | 23.79 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3144 | 162
2024-12-18 | 18:41 | 21.9394 | 85.3841 | 221.88 | 49.76 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3144 | 163
2024-12-18 | 18:41 | 21.9394 | 85.384 | 82.42 | 52.48 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3144 | 164
2024-12-18 | 18:41 | 21.9394 | 85.3839 | 219.14 | 49.76 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3144 | 165
2024-12-18 | 18:41 | 21.9394 | 85.3838 | 79.7 | 7.58 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3144 | 166
2024-12-18 | 18:41 | 21.9395 | 85.3838 | 36.16 | 15.57 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.12 | 167
2024-12-18 | 18:41 | 21.9396 | 85.3838 | 52.48 | 26.31 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1196 | 168
2024-12-18 | 18:41 | 21.9396 | 85.3839 | 68.8 | 10.12 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3144 | 169
2024-12-18 | 18:41 | 21.9396 | 85.3839 | 76.97 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 170
2024-12-18 | 18:41 | 21.9397 | 85.384 | 71.53 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 171
2024-12-18 | 18:41 | 21.9398 | 85.384 | 60.64 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1196 | 172
2024-12-18 | 18:41 | 21.9399 | 85.3839 | 55.2 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 173
2024-12-18 | 18:41 | 21.9399 | 85.3839 | 41.6 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 174
2024-12-18 | 18:41 | 21.94 | 85.3838 | 26.31 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 175
2024-12-18 | 18:41 | 21.9401 | 85.3838 | 12.8 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1192 | 176
2024-12-18 | 18:41 | 21.9401 | 85.3838 | 10.12 | 7.58 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 177
2024-12-18 | 18:41 | 21.9402 | 85.3837 | 47.04 | 3.16 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 178
2024-12-18 | 18:41 | 21.9403 | 85.3837 | 15.57 | 10.12 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1196 | 179
2024-12-18 | 18:41 | 21.9404 | 85.3836 | 33.45 | 3.16 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 180
2024-12-18 | 18:41 | 21.9405 | 85.3836 | 44.32 | 18.36 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1196 | 181
2024-12-18 | 18:42 | 21.9406 | 85.3835 | 33.45 | 3.16 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 182
2024-12-18 | 18:42 | 21.9406 | 85.3835 | 10.12 | 3.16 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 183
2024-12-18 | 18:42 | 21.9407 | 85.3834 | 10.12 | 1.39 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 184
2024-12-18 | 18:42 | 21.9408 | 85.3834 | 10.12 | 5.24 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1192 | 185
2024-12-18 | 18:42 | 21.9409 | 85.3833 | 12.8 | 3.16 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 186
2024-12-18 | 18:42 | 21.941 | 85.3832 | 10.12 | 1.39 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 187
2024-12-18 | 18:42 | 21.941 | 85.3831 | 5.24 | 7.58 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3139 | 188
2024-12-18 | 18:42 | 21.9411 | 85.3831 | 21.12 | 1.39 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1192 | 189
2024-12-18 | 18:42 | 21.9412 | 85.383 | 0 | 1.39 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 190
2024-12-18 | 18:42 | 21.9412 | 85.3829 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3144 | 191
2024-12-18 | 18:42 | 21.9413 | 85.3829 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1192 | 192
2024-12-18 | 18:42 | 21.9414 | 85.3828 | 0 | 5.24 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 193
2024-12-18 | 18:42 | 21.9415 | 85.3827 | 0 | 1.39 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 194
2024-12-18 | 18:42 | 21.9415 | 85.3826 | 0 | 1.39 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3144 | 195
2024-12-18 | 18:42 | 21.9416 | 85.3826 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1192 | 196
2024-12-18 | 18:42 | 21.9417 | 85.3825 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 197
2024-12-18 | 18:42 | 21.9418 | 85.3824 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 198
2024-12-18 | 18:42 | 21.9419 | 85.3824 | 0 | 15.57 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1196 | 199
2024-12-18 | 18:42 | 21.942 | 85.3824 | 18.36 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1196 | 200
2024-12-18 | 18:42 | 21.9421 | 85.3823 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 201
2024-12-18 | 18:42 | 21.9422 | 85.3823 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1196 | 202
2024-12-18 | 18:42 | 21.9423 | 85.3824 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1662 | 203
2024-12-18 | 18:42 | 21.9424 | 85.3824 | 0 | 3.16 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1192 | 204
2024-12-18 | 18:42 | 21.9425 | 85.3824 | 0 | 5.24 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1196 | 205
2024-12-18 | 18:42 | 21.9426 | 85.3825 | 0 | 1.39 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1662 | 206
2024-12-18 | 18:42 | 21.9426 | 85.3825 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0.094935 | 207
2024-12-18 | 18:42 | 21.9427 | 85.3825 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.12 | 208
2024-12-18 | 18:42 | 21.9428 | 85.3826 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 209
2024-12-18 | 18:42 | 21.9429 | 85.3826 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.12 | 210
2024-12-18 | 18:42 | 21.943 | 85.3827 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 211
2024-12-18 | 18:42 | 21.9431 | 85.3828 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 212
2024-12-18 | 18:43 | 21.9432 | 85.3828 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1192 | 213
2024-12-18 | 18:43 | 21.9432 | 85.3829 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3139 | 214
2024-12-18 | 18:43 | 21.9433 | 85.383 | 0 | 1.39 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1662 | 215
2024-12-18 | 18:43 | 21.9433 | 85.3831 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3139 | 216
2024-12-18 | 18:43 | 21.9434 | 85.3832 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1662 | 217
2024-12-18 | 18:43 | 21.9434 | 85.3833 | 0 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3135 | 218
2024-12-18 | 18:43 | 21.9434 | 85.3834 | 0 | 1.39 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3135 | 219
2024-12-18 | 18:43 | 21.9434 | 85.3835 | 0 | 1.39 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3135 | 220
2024-12-18 | 18:43 | 21.9435 | 85.3836 | 0 | 5.24 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1662 | 221
2024-12-18 | 18:43 | 21.9435 | 85.3837 | 0 | 3.16 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3139 | 222
2024-12-18 | 18:43 | 21.9436 | 85.3838 | 0 | 10.12 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 223
2024-12-18 | 18:43 | 21.9436 | 85.3839 | 0 | 10.12 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 10.3139 | 224
2024-12-18 | 18:43 | 21.9437 | 85.384 | 3.16 | 15.57 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1662 | 225
2024-12-18 | 18:43 | 21.9437 | 85.384 | 3.16 | 21.12 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 226
2024-12-18 | 18:43 | 21.9438 | 85.3841 | 10.12 | 26.31 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 227
2024-12-18 | 18:43 | 21.9438 | 85.3841 | 15.57 | 33.45 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0.094935 | 228
2024-12-18 | 18:43 | 21.9438 | 85.3841 | 26.31 | 26.31 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0.094935 | 229
2024-12-18 | 18:43 | 21.9439 | 85.3842 | 26.31 | 26.31 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 230
2024-12-18 | 18:43 | 21.9439 | 85.3842 | 30.73 | 23.79 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 231
2024-12-18 | 18:43 | 21.9439 | 85.3842 | 30.73 | 23.79 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 232
2024-12-18 | 18:43 | 21.9439 | 85.3842 | 30.73 | 23.79 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 233
2024-12-18 | 18:43 | 21.9439 | 85.3842 | 30.73 | 23.79 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 234
2024-12-18 | 18:43 | 21.9439 | 85.3842 | 30.73 | 23.79 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 235
2024-12-18 | 18:43 | 21.9439 | 85.3842 | 30.73 | 23.79 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 236
2024-12-18 | 18:43 | 21.9439 | 85.3842 | 30.73 | 23.79 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 237
2024-12-18 | 18:43 | 21.9439 | 85.3842 | 30.73 | 23.79 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 238
2024-12-18 | 18:43 | 21.9439 | 85.3842 | 30.73 | 23.79 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 239
2024-12-18 | 18:43 | 21.9439 | 85.3842 | 36.16 | 23.79 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 240
2024-12-18 | 18:43 | 21.9439 | 85.3842 | 41.6 | 18.36 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 241
2024-12-18 | 18:44 | 21.944 | 85.3842 | 44.32 | 7.58 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1192 | 242
2024-12-18 | 18:44 | 21.9441 | 85.3843 | 47.04 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 243
2024-12-18 | 18:44 | 21.9441 | 85.3843 | 49.76 | 0 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0 | 244
2024-12-18 | 18:44 | 21.9442 | 85.3843 | 36.16 | 3.16 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1192 | 245
2024-12-18 | 18:44 | 21.9443 | 85.3844 | 21.12 | 5.24 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1668 | 246
2024-12-18 | 18:44 | 21.9443 | 85.3844 | 15.57 | 7.58 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 0.094935 | 247
2024-12-18 | 18:44 | 21.9444 | 85.3844 | 10.12 | 1.39 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1196 | 248
2024-12-18 | 18:44 | 21.9445 | 85.3844 | 1.39 | 10.12 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1192 | 249
2024-12-18 | 18:44 | 21.9446 | 85.3844 | 7.58 | 1.39 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1196 | 250
2024-12-18 | 18:44 | 21.9447 | 85.3844 | 5.24 | 5.24 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1192 | 251
2024-12-18 | 18:44 | 21.9448 | 85.3844 | 1.39 | 1.39 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1196 | 252
2024-12-18 | 18:44 | 21.9449 | 85.3844 | 1.39 | 3.16 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1196 | 253
2024-12-18 | 18:44 | 21.945 | 85.3845 | 5.24 | 1.39 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 15.1665 | 254
2024-12-18 | 18:44 | 21.9451 | 85.3845 | 5.24 | 3.16 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1196 | 255
2024-12-18 | 18:44 | 21.9452 | 85.3845 | 5.24 | 1.39 | 6 | HAUL ROAD (HATHI CHOWK TO TWIN CANTEEN) | 11.1192 | 256
2024-12-18 | 18:44 | 21.9453 | 85.3845 | 10.12 | 1.39 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1192 | 257
2024-12-18 | 18:44 | 21.9454 | 85.3845 | 7.58 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1196 | 258
2024-12-18 | 18:44 | 21.9455 | 85.3845 | 5.24 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1196 | 259
2024-12-18 | 18:44 | 21.9456 | 85.3845 | 7.58 | 3.16 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1196 | 260
2024-12-18 | 18:44 | 21.9456 | 85.3845 | 18.36 | 1.39 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 0.094935 | 261
2024-12-18 | 18:44 | 21.9457 | 85.3846 | 5.24 | 5.24 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1665 | 262
2024-12-18 | 18:44 | 21.9458 | 85.3846 | 21.12 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1192 | 263
2024-12-18 | 18:44 | 21.9459 | 85.3846 | 5.24 | 5.24 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1192 | 264
2024-12-18 | 18:44 | 21.946 | 85.3846 | 21.12 | 1.39 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1196 | 265
2024-12-18 | 18:44 | 21.9461 | 85.3846 | 15.57 | 21.12 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1196 | 266
2024-12-18 | 18:44 | 21.9462 | 85.3847 | 60.64 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1665 | 267
2024-12-18 | 18:44 | 21.9463 | 85.3847 | 5.24 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.12 | 268
2024-12-18 | 18:44 | 21.9464 | 85.3847 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1196 | 269
2024-12-18 | 18:44 | 21.9465 | 85.3847 | 0 | 3.16 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1196 | 270
2024-12-18 | 18:44 | 21.9466 | 85.3848 | 3.16 | 18.36 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1665 | 271
2024-12-18 | 18:44 | 21.9466 | 85.3848 | 57.92 | 3.16 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 0.094935 | 272
2024-12-18 | 18:45 | 21.9468 | 85.3848 | 23.79 | 21.12 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 22.2392 | 273
2024-12-18 | 18:45 | 21.9468 | 85.3849 | 30.73 | 7.58 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 10.3144 | 274
2024-12-18 | 18:45 | 21.9469 | 85.3849 | 26.31 | 12.8 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1196 | 275
2024-12-18 | 18:45 | 21.947 | 85.3849 | 12.8 | 7.58 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1192 | 276
2024-12-18 | 18:45 | 21.9471 | 85.385 | 23.79 | 3.16 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1665 | 277
2024-12-18 | 18:45 | 21.9472 | 85.385 | 5.24 | 10.12 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1192 | 278
2024-12-18 | 18:45 | 21.9473 | 85.385 | 12.8 | 1.39 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1196 | 279
2024-12-18 | 18:45 | 21.9474 | 85.3851 | 10.12 | 15.57 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1665 | 280
2024-12-18 | 18:45 | 21.9475 | 85.3851 | 21.12 | 5.24 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1192 | 281
2024-12-18 | 18:45 | 21.9476 | 85.3852 | 15.57 | 12.8 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1665 | 282
2024-12-18 | 18:45 | 21.9477 | 85.3852 | 12.8 | 3.16 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1196 | 283
2024-12-18 | 18:45 | 21.9478 | 85.3853 | 12.8 | 5.24 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1665 | 284
2024-12-18 | 18:45 | 21.9479 | 85.3853 | 7.58 | 12.8 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1196 | 285
2024-12-18 | 18:45 | 21.948 | 85.3853 | 44.32 | 10.12 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1192 | 286
2024-12-18 | 18:45 | 21.948 | 85.3854 | 26.31 | 18.36 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 10.3135 | 287
2024-12-18 | 18:45 | 21.9481 | 85.3855 | 36.16 | 1.39 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1662 | 288
2024-12-18 | 18:45 | 21.9482 | 85.3855 | 3.16 | 3.16 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1192 | 289
2024-12-18 | 18:45 | 21.9483 | 85.3856 | 5.24 | 7.58 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1659 | 290
2024-12-18 | 18:45 | 21.9484 | 85.3856 | 36.16 | 23.79 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1196 | 291
2024-12-18 | 18:45 | 21.9485 | 85.3857 | 26.31 | 21.12 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1659 | 292
2024-12-18 | 18:45 | 21.9486 | 85.3857 | 44.32 | 12.8 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1196 | 293
2024-12-18 | 18:45 | 21.9487 | 85.3858 | 18.36 | 15.57 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1665 | 294
2024-12-18 | 18:45 | 21.9488 | 85.3859 | 23.79 | 10.12 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1662 | 295
2024-12-18 | 18:45 | 21.9488 | 85.3859 | 30.73 | 1.39 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 0 | 296
2024-12-18 | 18:45 | 21.9489 | 85.386 | 26.31 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1659 | 297
2024-12-18 | 18:45 | 21.9489 | 85.386 | 18.36 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 0.094935 | 298
2024-12-18 | 18:45 | 21.949 | 85.3861 | 10.12 | 3.16 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1662 | 299
2024-12-18 | 18:45 | 21.949 | 85.3861 | 5.24 | 1.39 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 0 | 300
2024-12-18 | 18:45 | 21.9491 | 85.3862 | 0 | 5.24 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1662 | 301
2024-12-18 | 18:46 | 21.9491 | 85.3862 | 0 | 3.16 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 0.094935 | 302
2024-12-18 | 18:46 | 21.9492 | 85.3862 | 1.39 | 3.16 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1196 | 303
2024-12-18 | 18:46 | 21.9492 | 85.3862 | 1.39 | 1.39 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 0 | 304
2024-12-18 | 18:46 | 21.9493 | 85.3863 | 1.39 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1659 | 305
2024-12-18 | 18:46 | 21.9493 | 85.3863 | 1.39 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 0 | 306
2024-12-18 | 18:46 | 21.9494 | 85.3863 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 11.1192 | 307
2024-12-18 | 18:46 | 21.9494 | 85.3863 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 0 | 308
2024-12-18 | 18:46 | 21.9495 | 85.3862 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1659 | 309
2024-12-18 | 18:46 | 21.9495 | 85.3862 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 0 | 310
2024-12-18 | 18:46 | 21.9495 | 85.3862 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 0 | 311
2024-12-18 | 18:46 | 21.9496 | 85.3861 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1659 | 312
2024-12-18 | 18:46 | 21.9496 | 85.3861 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 0 | 313
2024-12-18 | 18:46 | 21.9495 | 85.386 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 15.1659 | 314
2024-12-18 | 18:46 | 21.9495 | 85.3859 | 0 | 3.16 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 10.3135 | 315
2024-12-18 | 18:46 | 21.9495 | 85.3859 | 10.12 | 7.58 | 6 | HAUL ROAD (IM SECTION TO SUBGRADEDUMP) | 0 | 316
2024-12-18 | 18:46 | 21.9494 | 85.3858 | 21.12 | 3.16 | 6 | HAUL ROAD | 15.1659 | 317
2024-12-18 | 18:46 | 21.9494 | 85.3857 | 36.16 | 21.12 | 6 | HAUL ROAD | 10.313 | 318
2024-12-18 | 18:46 | 21.9494 | 85.3857 | 68.8 | 0 | 6 | HAUL ROAD | 0 | 319
2024-12-18 | 18:46 | 21.9493 | 85.3856 | 26.31 | 7.58 | 6 | HAUL ROAD | 15.1659 | 320
2024-12-18 | 18:46 | 21.9493 | 85.3855 | 55.2 | 26.31 | 6 | HAUL ROAD | 10.3135 | 321
2024-12-18 | 18:46 | 21.9493 | 85.3854 | 71.53 | 0 | 6 | HAUL ROAD | 10.3135 | 322
2024-12-18 | 18:46 | 21.9492 | 85.3853 | 23.79 | 10.12 | 6 | HAUL ROAD | 15.1659 | 323
2024-12-18 | 18:46 | 21.9492 | 85.3852 | 36.16 | 3.16 | 6 | HAUL ROAD | 10.3135 | 324
2024-12-18 | 18:46 | 21.9492 | 85.3852 | 38.88 | 15.57 | 6 | HAUL ROAD | 0 | 325
2024-12-18 | 18:46 | 21.9491 | 85.3851 | 23.79 | 5.24 | 6 | HAUL ROAD | 15.1662 | 326
2024-12-18 | 18:46 | 21.9491 | 85.385 | 26.31 | 0 | 6 | HAUL ROAD | 10.3139 | 327
2024-12-18 | 18:46 | 21.9491 | 85.3849 | 5.24 | 0 | 6 | HAUL ROAD | 10.3139 | 328
2024-12-18 | 18:46 | 21.949 | 85.3848 | 1.39 | 0 | 6 | HAUL ROAD | 15.1662 | 329
2024-12-18 | 18:46 | 21.949 | 85.3847 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 330
2024-12-18 | 18:46 | 21.949 | 85.3846 | 3.16 | 5.24 | 6 | HAUL ROAD | 10.3135 | 331
2024-12-18 | 18:46 | 21.949 | 85.3845 | 68.8 | 7.58 | 6 | HAUL ROAD | 10.3135 | 332
2024-12-18 | 18:47 | 21.949 | 85.3844 | 44.32 | 36.16 | 6 | HAUL ROAD | 10.3135 | 333
2024-12-18 | 18:47 | 21.9489 | 85.3843 | 90.59 | 12.8 | 6 | HAUL ROAD | 15.1662 | 334
2024-12-18 | 18:47 | 21.9489 | 85.3842 | 57.92 | 18.36 | 6 | HAUL ROAD | 10.3139 | 335
2024-12-18 | 18:47 | 21.9488 | 85.3841 | 74.25 | 7.58 | 6 | HAUL ROAD | 15.1659 | 336
2024-12-18 | 18:47 | 21.9488 | 85.384 | 36.16 | 10.12 | 6 | HAUL ROAD | 10.313 | 337
2024-12-18 | 18:47 | 21.9487 | 85.3839 | 30.73 | 1.39 | 6 | HAUL ROAD | 15.1662 | 338
2024-12-18 | 18:47 | 21.9486 | 85.3838 | 47.04 | 26.31 | 6 | HAUL ROAD | 15.1665 | 339
2024-12-18 | 18:47 | 21.9486 | 85.3837 | 23.79 | 3.16 | 6 | HAUL ROAD | 10.3135 | 340
2024-12-18 | 18:47 | 21.9485 | 85.3836 | 76.97 | 10.12 | 6 | HAUL ROAD | 15.1662 | 341
2024-12-18 | 18:47 | 21.9484 | 85.3835 | 52.48 | 47.04 | 6 | HAUL ROAD | 15.1659 | 342
2024-12-18 | 18:47 | 21.9483 | 85.3835 | 74.25 | 47.04 | 6 | HAUL ROAD | 11.1196 | 343
2024-12-18 | 18:47 | 21.9482 | 85.3834 | 117.87 | 7.58 | 6 | HAUL ROAD | 15.1659 | 344
2024-12-18 | 18:47 | 21.9481 | 85.3833 | 57.92 | 36.16 | 6 | HAUL ROAD | 15.1659 | 345
2024-12-18 | 18:47 | 21.9481 | 85.3832 | 49.76 | 10.12 | 6 | HAUL ROAD | 10.3139 | 346
2024-12-18 | 18:47 | 21.948 | 85.3831 | 49.76 | 10.12 | 6 | HAUL ROAD | 15.1662 | 347
2024-12-18 | 18:47 | 21.9479 | 85.383 | 36.16 | 26.31 | 6 | HAUL ROAD | 15.1659 | 348
2024-12-18 | 18:47 | 21.9478 | 85.3829 | 38.88 | 38.88 | 6 | HAUL ROAD | 15.1662 | 349
2024-12-18 | 18:47 | 21.9477 | 85.3828 | 76.97 | 7.58 | 6 | HAUL ROAD | 15.1665 | 350
2024-12-18 | 18:47 | 21.9476 | 85.3827 | 52.48 | 36.16 | 6 | HAUL ROAD | 15.1665 | 351
2024-12-18 | 18:47 | 21.9476 | 85.3826 | 33.45 | 5.24 | 6 | HAUL ROAD | 10.3139 | 352
2024-12-18 | 18:47 | 21.9475 | 85.3825 | 38.88 | 0 | 6 | HAUL ROAD | 15.1665 | 353
2024-12-18 | 18:47 | 21.9474 | 85.3824 | 0 | 0 | 6 | HAUL ROAD | 15.1665 | 354
2024-12-18 | 18:47 | 21.9474 | 85.3823 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 355
2024-12-18 | 18:47 | 21.9473 | 85.3822 | 0 | 0 | 6 | HAUL ROAD | 15.1665 | 356
2024-12-18 | 18:47 | 21.9473 | 85.3821 | 0 | 0 | 6 | HAUL ROAD | 10.3144 | 357
2024-12-18 | 18:47 | 21.9473 | 85.382 | 0 | 1.39 | 6 | HAUL ROAD | 10.3144 | 358
2024-12-18 | 18:47 | 21.9473 | 85.3819 | 18.36 | 55.2 | 6 | HAUL ROAD | 10.3144 | 359
2024-12-18 | 18:47 | 21.9473 | 85.3818 | 109.68 | 23.79 | 6 | HAUL ROAD | 10.3144 | 360
2024-12-18 | 18:47 | 21.9472 | 85.3817 | 33.45 | 12.8 | 6 | HAUL ROAD | 15.1665 | 361
2024-12-18 | 18:48 | 21.9472 | 85.3816 | 85.14 | 15.57 | 6 | HAUL ROAD | 10.3139 | 362
2024-12-18 | 18:48 | 21.9472 | 85.3815 | 30.73 | 47.04 | 6 | HAUL ROAD | 10.3139 | 363
2024-12-18 | 18:48 | 21.9471 | 85.3814 | 93.32 | 3.16 | 6 | HAUL ROAD | 15.1665 | 364
2024-12-18 | 18:48 | 21.9471 | 85.3813 | 47.04 | 41.6 | 6 | HAUL ROAD | 10.3139 | 365
2024-12-18 | 18:48 | 21.9471 | 85.3812 | 82.42 | 3.16 | 6 | HAUL ROAD | 10.3139 | 366
2024-12-18 | 18:48 | 21.947 | 85.3811 | 23.79 | 18.36 | 6 | HAUL ROAD | 15.1665 | 367
2024-12-18 | 18:48 | 21.947 | 85.381 | 38.88 | 5.24 | 6 | HAUL ROAD | 10.3144 | 368
2024-12-18 | 18:48 | 21.947 | 85.3809 | 23.79 | 18.36 | 6 | HAUL ROAD | 10.3144 | 369
2024-12-18 | 18:48 | 21.9469 | 85.3808 | 36.16 | 12.8 | 6 | HAUL ROAD | 15.1665 | 370
2024-12-18 | 18:48 | 21.9469 | 85.3807 | 33.45 | 30.73 | 6 | HAUL ROAD | 10.3139 | 371
2024-12-18 | 18:48 | 21.9469 | 85.3807 | 38.88 | 30.73 | 6 | HAUL ROAD | 0 | 372
2024-12-18 | 18:48 | 21.9468 | 85.3806 | 44.32 | 10.12 | 6 | HAUL ROAD | 15.1665 | 373
2024-12-18 | 18:48 | 21.9468 | 85.3805 | 49.76 | 47.04 | 6 | HAUL ROAD | 10.3144 | 374
2024-12-18 | 18:48 | 21.9467 | 85.3805 | 68.8 | 26.31 | 6 | HAUL ROAD | 11.12 | 375
2024-12-18 | 18:48 | 21.9466 | 85.3804 | 68.8 | 68.8 | 6 | HAUL ROAD | 15.1665 | 376
2024-12-18 | 18:48 | 21.9466 | 85.3804 | 71.53 | 15.57 | 6 | HAUL ROAD | 0.094935 | 377
2024-12-18 | 18:48 | 21.9465 | 85.3803 | 26.31 | 30.73 | 6 | HAUL ROAD | 15.1665 | 378
2024-12-18 | 18:48 | 21.9464 | 85.3803 | 44.32 | 12.8 | 6 | HAUL ROAD | 11.1196 | 379
2024-12-18 | 18:48 | 21.9463 | 85.3803 | 63.36 | 49.76 | 6 | HAUL ROAD | 11.1196 | 380
2024-12-18 | 18:48 | 21.9462 | 85.3803 | 74.25 | 47.04 | 6 | HAUL ROAD | 11.12 | 381
2024-12-18 | 18:48 | 21.9461 | 85.3802 | 66.08 | 57.92 | 6 | HAUL ROAD | 15.1665 | 382
2024-12-18 | 18:48 | 21.946 | 85.3802 | 85.14 | 10.12 | 6 | HAUL ROAD | 11.1196 | 383
2024-12-18 | 18:48 | 21.9459 | 85.3802 | 26.31 | 33.45 | 6 | HAUL ROAD | 11.1196 | 384
2024-12-18 | 18:48 | 21.9458 | 85.3802 | 79.7 | 1.39 | 6 | HAUL ROAD | 11.1192 | 385
2024-12-18 | 18:48 | 21.9457 | 85.3802 | 15.57 | 0 | 6 | HAUL ROAD | 11.1192 | 386
2024-12-18 | 18:48 | 21.9457 | 85.3801 | 0 | 3.16 | 6 | HAUL ROAD | 10.3139 | 387
2024-12-18 | 18:48 | 21.9456 | 85.3801 | 0 | 5.24 | 6 | HAUL ROAD | 11.1196 | 388
2024-12-18 | 18:48 | 21.9455 | 85.38 | 0 | 5.24 | 6 | HAUL ROAD | 15.1665 | 389
2024-12-18 | 18:48 | 21.9455 | 85.38 | 0 | 10.12 | 6 | HAUL ROAD | 0 | 390
2024-12-18 | 18:48 | 21.9454 | 85.3799 | 0 | 18.36 | 6 | HAUL ROAD | 15.1665 | 391
2024-12-18 | 18:48 | 21.9454 | 85.3798 | 1.39 | 26.31 | 6 | HAUL ROAD | 10.3139 | 392
2024-12-18 | 18:49 | 21.9454 | 85.3797 | 7.58 | 38.88 | 6 | HAUL ROAD | 10.3139 | 393
2024-12-18 | 18:49 | 21.9454 | 85.3796 | 23.79 | 18.36 | 6 | HAUL ROAD | 10.3139 | 394
2024-12-18 | 18:49 | 21.9454 | 85.3796 | 18.36 | 0 | 6 | HAUL ROAD | 0 | 395
2024-12-18 | 18:49 | 21.9453 | 85.3795 | 1.39 | 0 | 6 | HAUL ROAD | 15.1665 | 396
2024-12-18 | 18:49 | 21.9453 | 85.3795 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 397
2024-12-18 | 18:49 | 21.9453 | 85.3795 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 398
2024-12-18 | 18:49 | 21.9453 | 85.3795 | 0 | 0 | 6 | HAUL ROAD | 0 | 399
2024-12-18 | 18:49 | 21.9453 | 85.3795 | 0 | 0 | 6 | HAUL ROAD | 0 | 400
2024-12-18 | 18:49 | 21.9453 | 85.3794 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 401
2024-12-18 | 18:49 | 21.9453 | 85.3794 | 0 | 0 | 6 | HAUL ROAD | 0 | 402
2024-12-18 | 18:49 | 21.9453 | 85.3793 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 403
2024-12-18 | 18:49 | 21.9453 | 85.3793 | 0 | 0 | 6 | HAUL ROAD | 0 | 404
2024-12-18 | 18:49 | 21.9453 | 85.3792 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 405
2024-12-18 | 18:49 | 21.9453 | 85.3791 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 406
2024-12-18 | 18:49 | 21.9453 | 85.3791 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 407
2024-12-18 | 18:49 | 21.9453 | 85.379 | 0 | 1.39 | 6 | HAUL ROAD | 10.3135 | 408
2024-12-18 | 18:49 | 21.9453 | 85.3789 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 409
2024-12-18 | 18:49 | 21.9453 | 85.3788 | 0 | 1.39 | 6 | HAUL ROAD | 10.3135 | 410
2024-12-18 | 18:49 | 21.9454 | 85.3788 | 0 | 3.16 | 6 | HAUL ROAD | 11.1196 | 411
2024-12-18 | 18:49 | 21.9455 | 85.3788 | 0 | 5.24 | 6 | HAUL ROAD | 11.1196 | 412
2024-12-18 | 18:49 | 21.9455 | 85.3787 | 0 | 7.58 | 6 | HAUL ROAD | 10.3135 | 413
2024-12-18 | 18:49 | 21.9456 | 85.3787 | 0 | 23.79 | 6 | HAUL ROAD | 11.1196 | 414
2024-12-18 | 18:49 | 21.9457 | 85.3787 | 7.58 | 57.92 | 6 | HAUL ROAD | 11.1196 | 415
2024-12-18 | 18:49 | 21.9458 | 85.3787 | 285.11 | 359.61 | 6 | HAUL ROAD | 11.1192 | 416
2024-12-18 | 18:49 | 21.9458 | 85.3787 | 304.4 | 0 | 6 | HAUL ROAD | 0 | 417
2024-12-18 | 18:49 | 21.9459 | 85.3787 | 71.53 | 1.39 | 6 | HAUL ROAD | 11.1192 | 418
2024-12-18 | 18:49 | 21.9459 | 85.3787 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 419
2024-12-18 | 18:49 | 21.9459 | 85.3787 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 420
2024-12-18 | 18:49 | 21.9459 | 85.3787 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 421
2024-12-18 | 18:50 | 21.9459 | 85.3787 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 422
2024-12-18 | 18:50 | 21.946 | 85.3787 | 0 | 1.39 | 6 | HAUL ROAD | 11.1196 | 423
2024-12-18 | 18:50 | 21.9461 | 85.3788 | 0 | 0 | 6 | HAUL ROAD | 15.1665 | 424
2024-12-18 | 18:50 | 21.9461 | 85.3788 | 0 | 0 | 6 | HAUL ROAD | 0 | 425
2024-12-18 | 18:50 | 21.9462 | 85.3789 | 0 | 1.39 | 6 | HAUL ROAD | 15.1665 | 426
2024-12-18 | 18:50 | 21.9463 | 85.3789 | 0 | 1.39 | 6 | HAUL ROAD | 11.12 | 427
2024-12-18 | 18:50 | 21.9463 | 85.379 | 0 | 7.58 | 6 | HAUL ROAD | 10.3144 | 428
2024-12-18 | 18:50 | 21.9464 | 85.3791 | 0 | 10.12 | 6 | HAUL ROAD | 15.1665 | 429
2024-12-18 | 18:50 | 21.9465 | 85.3791 | 0 | 23.79 | 6 | HAUL ROAD | 11.1196 | 430
2024-12-18 | 18:50 | 21.9465 | 85.3792 | 0 | 41.6 | 6 | HAUL ROAD | 10.3144 | 431
2024-12-18 | 18:50 | 21.9466 | 85.3792 | 10.12 | 85.14 | 6 | HAUL ROAD | 11.1196 | 432
2024-12-18 | 18:50 | 21.9466 | 85.3793 | 57.92 | 191.71 | 6 | HAUL ROAD | 10.3144 | 433
2024-12-18 | 18:50 | 21.9467 | 85.3794 | 323.71 | 26.31 | 6 | HAUL ROAD | 15.1665 | 434
2024-12-18 | 18:50 | 21.9467 | 85.3794 | 1.39 | 0 | 6 | HAUL ROAD | 0 | 435
2024-12-18 | 18:50 | 21.9467 | 85.3795 | 0 | 0 | 6 | HAUL ROAD | 10.3139 | 436
2024-12-18 | 18:50 | 21.9468 | 85.3795 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 437
2024-12-18 | 18:50 | 21.9468 | 85.3795 | 0 | 0 | 6 | HAUL ROAD | 0 | 438
2024-12-18 | 18:50 | 21.9468 | 85.3795 | 0 | 0 | 6 | HAUL ROAD | 0 | 439
2024-12-18 | 18:50 | 21.9469 | 85.3796 | 0 | 0 | 6 | HAUL ROAD | 15.1665 | 440
2024-12-18 | 18:50 | 21.9469 | 85.3796 | 0 | 0 | 6 | HAUL ROAD | 0 | 441
2024-12-18 | 18:50 | 21.9469 | 85.3796 | 0 | 0 | 6 | HAUL ROAD | 0 | 442
2024-12-18 | 18:50 | 21.947 | 85.3797 | 0 | 0 | 6 | HAUL ROAD | 15.1665 | 443
2024-12-18 | 18:50 | 21.947 | 85.3797 | 0 | 0 | 6 | HAUL ROAD | 0.13426 | 444
2024-12-18 | 18:50 | 21.947 | 85.3797 | 0 | 0 | 6 | HAUL ROAD | 0.13426 | 445
2024-12-18 | 18:50 | 21.9469 | 85.3798 | 0 | 0 | 6 | HAUL ROAD | 15.1665 | 446
2024-12-18 | 18:50 | 21.9469 | 85.3798 | 0 | 0 | 6 | HAUL ROAD | 0 | 447
2024-12-18 | 18:50 | 21.9469 | 85.3798 | 0 | 0 | 6 | HAUL ROAD | 0 | 448
2024-12-18 | 18:50 | 21.9469 | 85.3798 | 0 | 0 | 6 | HAUL ROAD | 0 | 449
2024-12-18 | 18:50 | 21.9468 | 85.3797 | 0 | 0 | 6 | HAUL ROAD | 15.1665 | 450
2024-12-18 | 18:50 | 21.9468 | 85.3797 | 0 | 0 | 6 | HAUL ROAD | 0 | 451
2024-12-18 | 18:50 | 21.9468 | 85.3797 | 0 | 0 | 6 | HAUL ROAD | 0 | 452
2024-12-18 | 18:51 | 21.9467 | 85.3796 | 0 | 0 | 6 | HAUL ROAD | 15.1665 | 453
2024-12-18 | 18:51 | 21.9467 | 85.3796 | 0 | 0 | 6 | HAUL ROAD | 0 | 454
2024-12-18 | 18:51 | 21.9466 | 85.3796 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 455
2024-12-18 | 18:51 | 21.9466 | 85.3796 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 456
2024-12-18 | 18:51 | 21.9466 | 85.3795 | 0 | 0 | 6 | HAUL ROAD | 10.3144 | 457
2024-12-18 | 18:51 | 21.9466 | 85.3795 | 0 | 12.8 | 6 | HAUL ROAD | 0.094935 | 458
2024-12-18 | 18:51 | 21.9466 | 85.3794 | 5.24 | 60.64 | 6 | HAUL ROAD | 10.3144 | 459
2024-12-18 | 18:51 | 21.9466 | 85.3793 | 47.04 | 63.36 | 6 | HAUL ROAD | 10.3144 | 460
2024-12-18 | 18:51 | 21.9465 | 85.3793 | 57.92 | 0 | 6 | HAUL ROAD | 11.1196 | 461
2024-12-18 | 18:51 | 21.9465 | 85.3792 | 10.12 | 0 | 6 | HAUL ROAD | 10.3144 | 462
2024-12-18 | 18:51 | 21.9464 | 85.3792 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 463
2024-12-18 | 18:51 | 21.9464 | 85.3791 | 0 | 0 | 6 | HAUL ROAD | 10.3139 | 464
2024-12-18 | 18:51 | 21.9463 | 85.3791 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 465
2024-12-18 | 18:51 | 21.9463 | 85.379 | 0 | 1.39 | 6 | HAUL ROAD | 10.3144 | 466
2024-12-18 | 18:51 | 21.9462 | 85.379 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 467
2024-12-18 | 18:51 | 21.9462 | 85.3789 | 0 | 3.16 | 6 | HAUL ROAD | 10.3144 | 468
2024-12-18 | 18:51 | 21.9461 | 85.3789 | 0 | 1.39 | 6 | HAUL ROAD | 11.1196 | 469
2024-12-18 | 18:51 | 21.946 | 85.3788 | 0 | 5.24 | 6 | HAUL ROAD | 15.1665 | 470
2024-12-18 | 18:51 | 21.946 | 85.3788 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 471
2024-12-18 | 18:51 | 21.9459 | 85.3788 | 0 | 36.16 | 6 | HAUL ROAD | 11.1196 | 472
2024-12-18 | 18:51 | 21.9458 | 85.3788 | 15.57 | 85.14 | 6 | HAUL ROAD | 11.1192 | 473
2024-12-18 | 18:51 | 21.9458 | 85.3788 | 52.48 | 145.18 | 6 | HAUL ROAD | 0 | 474
2024-12-18 | 18:51 | 21.9457 | 85.3788 | 38.88 | 0 | 6 | HAUL ROAD | 11.1192 | 475
2024-12-18 | 18:51 | 21.9456 | 85.3788 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 476
2024-12-18 | 18:51 | 21.9455 | 85.3788 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 477
2024-12-18 | 18:51 | 21.9455 | 85.3789 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 478
2024-12-18 | 18:51 | 21.9454 | 85.3789 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 479
2024-12-18 | 18:51 | 21.9454 | 85.379 | 0 | 0 | 6 | HAUL ROAD | 10.3139 | 480
2024-12-18 | 18:51 | 21.9453 | 85.379 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 481
2024-12-18 | 18:52 | 21.9453 | 85.3791 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 482
2024-12-18 | 18:52 | 21.9453 | 85.3792 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 483
2024-12-18 | 18:52 | 21.9453 | 85.3793 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 484
2024-12-18 | 18:52 | 21.9454 | 85.3794 | 0 | 0 | 6 | HAUL ROAD | 15.1665 | 485
2024-12-18 | 18:52 | 21.9454 | 85.3795 | 0 | 0 | 6 | HAUL ROAD | 10.3139 | 486
2024-12-18 | 18:52 | 21.9454 | 85.3795 | 1.39 | 1.39 | 6 | HAUL ROAD | 0 | 487
2024-12-18 | 18:52 | 21.9454 | 85.3796 | 10.12 | 0 | 6 | HAUL ROAD | 10.3139 | 488
2024-12-18 | 18:52 | 21.9454 | 85.3797 | 18.36 | 0 | 6 | HAUL ROAD | 10.3139 | 489
2024-12-18 | 18:52 | 21.9454 | 85.3798 | 5.24 | 0 | 6 | HAUL ROAD | 10.3139 | 490
2024-12-18 | 18:52 | 21.9454 | 85.3798 | 0 | 0 | 6 | HAUL ROAD | 0 | 491
2024-12-18 | 18:52 | 21.9453 | 85.3799 | 1.39 | 0 | 6 | HAUL ROAD | 15.1665 | 492
2024-12-18 | 18:52 | 21.9453 | 85.3798 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 493
2024-12-18 | 18:52 | 21.9452 | 85.3798 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 494
2024-12-18 | 18:52 | 21.9452 | 85.3797 | 3.16 | 3.16 | 6 | HAUL ROAD | 10.3135 | 495
2024-12-18 | 18:52 | 21.9451 | 85.3796 | 5.24 | 0 | 6 | HAUL ROAD | 15.1662 | 496
2024-12-18 | 18:52 | 21.9451 | 85.3795 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 10.3139 | 497
2024-12-18 | 18:52 | 21.9451 | 85.3794 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 10.3139 | 498
2024-12-18 | 18:52 | 21.945 | 85.3793 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 15.1665 | 499
2024-12-18 | 18:52 | 21.945 | 85.3792 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 10.3139 | 500
2024-12-18 | 18:52 | 21.9449 | 85.379 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 23.4338 | 501
2024-12-18 | 18:52 | 21.9449 | 85.3789 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 10.3139 | 502
2024-12-18 | 18:52 | 21.9449 | 85.3789 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 503
2024-12-18 | 18:52 | 21.9448 | 85.3788 | 0 | 1.39 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 15.1665 | 504
2024-12-18 | 18:52 | 21.9448 | 85.3787 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 10.3139 | 505
2024-12-18 | 18:52 | 21.9447 | 85.3786 | 0 | 5.24 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 15.1665 | 506
2024-12-18 | 18:52 | 21.9447 | 85.3785 | 0 | 10.12 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 10.3139 | 507
2024-12-18 | 18:52 | 21.9446 | 85.3785 | 0 | 21.12 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 11.1192 | 508
2024-12-18 | 18:52 | 21.9445 | 85.3785 | 0 | 60.64 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 11.1196 | 509
2024-12-18 | 18:52 | 21.9444 | 85.3785 | 1.39 | 49.76 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 11.1192 | 510
2024-12-18 | 18:52 | 21.9443 | 85.3784 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 15.1665 | 511
2024-12-18 | 18:52 | 21.9443 | 85.3784 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0.094935 | 512
2024-12-18 | 18:53 | 21.9442 | 85.3784 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 11.12 | 513
2024-12-18 | 18:53 | 21.9441 | 85.3784 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 11.1192 | 514
2024-12-18 | 18:53 | 21.9441 | 85.3784 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 515
2024-12-18 | 18:53 | 21.9441 | 85.3784 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 516
2024-12-18 | 18:53 | 21.9441 | 85.3785 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 10.3135 | 517
2024-12-18 | 18:53 | 21.944 | 85.3785 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 11.1196 | 518
2024-12-18 | 18:53 | 21.944 | 85.3784 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 10.3144 | 519
2024-12-18 | 18:53 | 21.9439 | 85.3784 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 11.1192 | 520
2024-12-18 | 18:53 | 21.944 | 85.3784 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 11.1192 | 521
2024-12-18 | 18:53 | 21.944 | 85.3783 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 10.3144 | 522
2024-12-18 | 18:53 | 21.944 | 85.3784 | 0 | 1.39 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 10.3144 | 523
2024-12-18 | 18:53 | 21.9441 | 85.3784 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 11.1196 | 524
2024-12-18 | 18:53 | 21.9441 | 85.3784 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 525
2024-12-18 | 18:53 | 21.9442 | 85.3784 | 0 | 1.39 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 11.1192 | 526
2024-12-18 | 18:53 | 21.9442 | 85.3784 | 0 | 1.39 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 527
2024-12-18 | 18:53 | 21.9443 | 85.3785 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 15.1668 | 528
2024-12-18 | 18:53 | 21.9443 | 85.3785 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0.094935 | 529
2024-12-18 | 18:53 | 21.9444 | 85.3786 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 15.1665 | 530
2024-12-18 | 18:53 | 21.9444 | 85.3786 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 531
2024-12-18 | 18:53 | 21.9443 | 85.3787 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 15.1665 | 532
2024-12-18 | 18:53 | 21.9443 | 85.3787 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0.094935 | 533
2024-12-18 | 18:53 | 21.9443 | 85.3787 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0.094935 | 534
2024-12-18 | 18:53 | 21.9442 | 85.3787 | 0 | 1.39 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 11.12 | 535
2024-12-18 | 18:53 | 21.9442 | 85.3787 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 536
2024-12-18 | 18:53 | 21.9442 | 85.3787 | 0 | 3.16 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 537
2024-12-18 | 18:53 | 21.9441 | 85.3787 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 11.1192 | 538
2024-12-18 | 18:53 | 21.9441 | 85.3787 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 539
2024-12-18 | 18:53 | 21.9441 | 85.3787 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 540
2024-12-18 | 18:53 | 21.9441 | 85.3786 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 10.3135 | 541
2024-12-18 | 18:54 | 21.944 | 85.3786 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 11.1196 | 542
2024-12-18 | 18:54 | 21.944 | 85.3786 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 543
2024-12-18 | 18:54 | 21.944 | 85.3786 | 0 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 544
2024-12-18 | 18:54 | 21.944 | 85.3787 | 5.24 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 10.3144 | 545
2024-12-18 | 18:54 | 21.944 | 85.3787 | 23.79 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 546
2024-12-18 | 18:54 | 21.9439 | 85.3787 | 52.48 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 11.1192 | 547
2024-12-18 | 18:54 | 21.944 | 85.3787 | 68.8 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 11.1192 | 548
2024-12-18 | 18:54 | 21.944 | 85.3787 | 90.59 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 549
2024-12-18 | 18:54 | 21.944 | 85.3787 | 90.59 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 550
2024-12-18 | 18:54 | 21.944 | 85.3787 | 90.59 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 551
2024-12-18 | 18:54 | 21.944 | 85.3787 | 90.59 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 552
2024-12-18 | 18:54 | 21.944 | 85.3787 | 90.59 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 553
2024-12-18 | 18:54 | 21.944 | 85.3787 | 90.59 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 554
2024-12-18 | 18:54 | 21.944 | 85.3787 | 90.59 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 555
2024-12-18 | 18:54 | 21.944 | 85.3787 | 90.59 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 556
2024-12-18 | 18:54 | 21.944 | 85.3787 | 90.59 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 557
2024-12-18 | 18:54 | 21.944 | 85.3787 | 90.59 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 558
2024-12-18 | 18:54 | 21.944 | 85.3787 | 90.59 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 559
2024-12-18 | 18:54 | 21.944 | 85.3787 | 60.64 | 0 | 6 | HAUL ROAD (SUBGRADE TO 710RL) | 0 | 560
2024-12-18 | 18:54 | 21.944 | 85.3788 | 87.87 | 0 | 2.1 | DRILL 664 KH-1 PIT-2 | 10.3144 | 561
2024-12-18 | 18:54 | 21.9439 | 85.3788 | 26.31 | 0 | 2.2 | DRILL 664 KH-1 PIT-2 (HOLE) | 11.1192 | 562
2024-12-18 | 18:54 | 21.9439 | 85.3788 | 33.45 | 0 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 563
2024-12-18 | 18:54 | 21.944 | 85.3788 | 44.32 | 1.39 | 2.1 | DRILL 664 KH-1 PIT-2 | 11.1192 | 564
2024-12-18 | 18:54 | 21.944 | 85.3788 | 98.77 | 3.16 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 565
2024-12-18 | 18:54 | 21.944 | 85.3788 | 0 | 1.39 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 566
2024-12-18 | 18:54 | 21.944 | 85.3788 | 0 | 5.24 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 567
2024-12-18 | 18:54 | 21.944 | 85.3788 | 3.16 | 3.16 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 568
2024-12-18 | 18:54 | 21.944 | 85.3788 | 0 | 3.16 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 569
2024-12-18 | 18:54 | 21.944 | 85.3788 | 0 | 1.39 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 570
2024-12-18 | 18:54 | 21.944 | 85.3788 | 1.39 | 3.16 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 571
2024-12-18 | 18:54 | 21.944 | 85.3788 | 1.39 | 1.39 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 572
2024-12-18 | 18:55 | 21.944 | 85.3788 | 1.39 | 5.24 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 573
2024-12-18 | 18:55 | 21.944 | 85.3788 | 1.39 | 1.39 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 574
2024-12-18 | 18:55 | 21.944 | 85.3788 | 7.58 | 5.24 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 575
2024-12-18 | 18:55 | 21.944 | 85.3788 | 1.39 | 5.24 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 576
2024-12-18 | 18:55 | 21.944 | 85.3788 | 10.12 | 5.24 | 2.2 | DRILL 664 KH-1 PIT-2 (HOLE) | 0 | 577
2024-12-18 | 18:55 | 21.944 | 85.3788 | 7.58 | 5.24 | 2.2 | DRILL 664 KH-1 PIT-2 (HOLE) | 0 | 578
2024-12-18 | 18:55 | 21.944 | 85.3788 | 0 | 3.16 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 579
2024-12-18 | 18:55 | 21.944 | 85.3788 | 1.39 | 3.16 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 580
2024-12-18 | 18:55 | 21.944 | 85.3788 | 0 | 3.16 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 581
2024-12-18 | 18:55 | 21.944 | 85.3788 | 0 | 3.16 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 582
2024-12-18 | 18:55 | 21.944 | 85.3788 | 0 | 5.24 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 583
2024-12-18 | 18:55 | 21.944 | 85.3788 | 18.36 | 1.39 | 2.2 | DRILL 664 KH-1 PIT-2 (HOLE) | 0 | 584
2024-12-18 | 18:55 | 21.944 | 85.3789 | 428.86 | 3.16 | 5 | DRILL 664 KH-1 PIT-2 (CABIN) | 10.3144 | 585
2024-12-18 | 18:55 | 21.944 | 85.3789 | 169.8 | 1.39 | 2.2 | DRILL 664 KH-1 PIT-2 (HOLE) | 0 | 586
2024-12-18 | 18:55 | 21.944 | 85.3789 | 5.24 | 76.97 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 587
2024-12-18 | 18:55 | 21.944 | 85.3789 | 5.24 | 74.25 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 588
2024-12-18 | 18:55 | 21.944 | 85.3789 | 21.12 | 63.36 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 589
2024-12-18 | 18:55 | 21.944 | 85.3789 | 12.8 | 104.23 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 590
2024-12-18 | 18:55 | 21.944 | 85.3789 | 26.31 | 66.08 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 591
2024-12-18 | 18:55 | 21.944 | 85.3789 | 33.45 | 74.25 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 592
2024-12-18 | 18:55 | 21.944 | 85.3789 | 21.12 | 82.42 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 593
2024-12-18 | 18:55 | 21.944 | 85.3789 | 15.57 | 90.59 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 594
2024-12-18 | 18:55 | 21.944 | 85.3789 | 18.36 | 98.77 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 595
2024-12-18 | 18:56 | 21.944 | 85.3789 | 18.36 | 106.96 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 596
2024-12-18 | 18:56 | 21.944 | 85.3789 | 36.16 | 153.39 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 597
2024-12-18 | 18:56 | 21.944 | 85.3789 | 33.45 | 120.6 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 598
2024-12-18 | 18:56 | 21.944 | 85.3789 | 12.8 | 147.92 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 599
2024-12-18 | 18:56 | 21.944 | 85.3789 | 18.36 | 87.87 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 600
2024-12-18 | 18:56 | 21.944 | 85.3789 | 23.79 | 66.08 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 601
2024-12-18 | 18:56 | 21.944 | 85.3789 | 15.57 | 47.04 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 602
2024-12-18 | 18:56 | 21.944 | 85.3789 | 3.16 | 12.8 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 603
2024-12-18 | 18:56 | 21.944 | 85.3789 | 3.16 | 33.45 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 604
2024-12-18 | 18:56 | 21.944 | 85.3789 | 5.24 | 41.6 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 605
2024-12-18 | 18:56 | 21.944 | 85.3789 | 12.8 | 26.31 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 606
2024-12-18 | 18:56 | 21.944 | 85.3789 | 10.12 | 10.12 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 607
2024-12-18 | 18:56 | 21.944 | 85.3789 | 0 | 0 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 608
2024-12-18 | 18:56 | 21.944 | 85.3789 | 0 | 18.36 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 609
2024-12-18 | 18:56 | 21.944 | 85.3789 | 3.16 | 57.92 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 610
2024-12-18 | 18:56 | 21.944 | 85.3789 | 3.16 | 41.6 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 611
2024-12-18 | 18:56 | 21.944 | 85.3789 | 0 | 71.53 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 612
2024-12-18 | 18:56 | 21.944 | 85.3789 | 3.16 | 66.08 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 613
2024-12-18 | 18:56 | 21.944 | 85.3789 | 3.16 | 26.31 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 614
2024-12-18 | 18:57 | 21.9439 | 85.3789 | 47.04 | 3.16 | 2.1 | DRILL 664 KH-1 PIT-2 | 11.1192 | 615
2024-12-18 | 18:57 | 21.944 | 85.3789 | 221.88 | 0 | 5 | DRILL 664 KH-1 PIT-2 (CABIN) | 11.1192 | 616
2024-12-18 | 18:57 | 21.944 | 85.3789 | 49.76 | 5.24 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 617
2024-12-18 | 18:57 | 21.944 | 85.3789 | 123.33 | 5.24 | 5 | DRILL 664 KH-1 PIT-2 (CABIN) | 0 | 618
2024-12-18 | 18:57 | 21.944 | 85.3789 | 7.58 | 23.79 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 619
2024-12-18 | 18:57 | 21.944 | 85.3789 | 41.6 | 7.58 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 620
2024-12-18 | 18:57 | 21.944 | 85.3789 | 18.36 | 0 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 621
2024-12-18 | 18:57 | 21.944 | 85.3789 | 26.31 | 7.58 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 622
2024-12-18 | 18:57 | 21.944 | 85.3789 | 60.64 | 33.45 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 623
2024-12-18 | 18:57 | 21.944 | 85.3789 | 36.16 | 41.6 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 624
2024-12-18 | 18:57 | 21.944 | 85.3789 | 49.76 | 38.88 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 625
2024-12-18 | 18:57 | 21.944 | 85.3789 | 44.32 | 26.31 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 626
2024-12-18 | 18:57 | 21.944 | 85.3789 | 49.76 | 23.79 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 627
2024-12-18 | 18:57 | 21.944 | 85.3789 | 60.64 | 36.16 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 628
2024-12-18 | 18:57 | 21.944 | 85.3789 | 44.32 | 38.88 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 629
2024-12-18 | 18:57 | 21.944 | 85.3789 | 47.04 | 38.88 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 630
2024-12-18 | 18:57 | 21.944 | 85.3789 | 82.42 | 3.16 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 631
2024-12-18 | 18:57 | 21.944 | 85.3789 | 74.25 | 10.12 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 632
2024-12-18 | 18:57 | 21.944 | 85.3789 | 74.25 | 5.24 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 633
2024-12-18 | 18:57 | 21.944 | 85.3789 | 55.2 | 5.24 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 634
2024-12-18 | 18:57 | 21.944 | 85.3789 | 167.07 | 57.92 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 635
2024-12-18 | 18:57 | 21.944 | 85.3789 | 76.97 | 0 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 636
2024-12-18 | 18:57 | 21.944 | 85.3789 | 96.05 | 49.76 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 637
2024-12-18 | 18:57 | 21.944 | 85.3789 | 57.92 | 3.16 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 638
2024-12-18 | 18:57 | 21.944 | 85.3789 | 36.16 | 26.31 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 639
2024-12-18 | 18:57 | 21.944 | 85.3789 | 41.6 | 26.31 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 640
2024-12-18 | 18:58 | 21.944 | 85.3789 | 49.76 | 7.58 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 641
2024-12-18 | 18:58 | 21.944 | 85.3789 | 147.92 | 18.36 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 642
2024-12-18 | 18:58 | 21.944 | 85.3789 | 249.35 | 3.16 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 643
2024-12-18 | 18:58 | 21.944 | 85.3789 | 93.32 | 18.36 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 644
2024-12-18 | 18:58 | 21.944 | 85.3789 | 101.5 | 44.32 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 645
2024-12-18 | 18:58 | 21.9439 | 85.3788 | 136.99 | 307.16 | 2.1 | DRILL 664 KH-1 PIT-2 | 15.1665 | 646
2024-12-18 | 18:58 | 21.9439 | 85.3788 | 66.08 | 331.99 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 647
2024-12-18 | 18:58 | 21.9439 | 85.3788 | 123.33 | 337.51 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 648
2024-12-18 | 18:58 | 21.944 | 85.3788 | 180.75 | 304.4 | 2.1 | DRILL 664 KH-1 PIT-2 | 11.1192 | 649
2024-12-18 | 18:58 | 21.944 | 85.3788 | 167.07 | 381.75 | 5 | DRILL 664 KH-1 PIT-2 (CABIN) | 0 | 650
2024-12-18 | 18:58 | 21.944 | 85.3788 | 249.35 | 392.82 | 5 | DRILL 664 KH-1 PIT-2 (CABIN) | 0 | 651
2024-12-18 | 18:58 | 21.944 | 85.3788 | 296.13 | 373.44 | 5 | DRILL 664 KH-1 PIT-2 (CABIN) | 0 | 652
2024-12-18 | 18:59 | 21.944 | 85.3788 | 331.99 | 301.64 | 5 | DRILL 664 KH-1 PIT-2 (CABIN) | 0 | 653
2024-12-18 | 18:59 | 21.944 | 85.3788 | 243.85 | 381.75 | 5 | DRILL 664 KH-1 PIT-2 (CABIN) | 0 | 654
2024-12-18 | 18:59 | 21.944 | 85.3788 | 390.05 | 384.51 | 5 | DRILL 664 KH-1 PIT-2 (CABIN) | 0 | 655
2024-12-18 | 18:59 | 21.944 | 85.3788 | 409.44 | 60.64 | 5 | DRILL 664 KH-1 PIT-2 (CABIN) | 0 | 656
2024-12-18 | 18:59 | 21.944 | 85.3788 | 243.85 | 128.79 | 2.1 | DRILL 664 KH-1 PIT-2 | 0 | 657
2024-12-18 | 19:02 | 21.9434 | 85.3789 | 44.32 | 93.32 | 2.1 | ROC L8 KH-1 PIT-2 | 67.5095 | 658
2024-12-18 | 19:02 | 21.9434 | 85.3789 | 26.31 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 659
2024-12-18 | 19:02 | 21.9434 | 85.3789 | 44.32 | 126.06 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 660
2024-12-18 | 19:02 | 21.9434 | 85.3789 | 15.57 | 183.49 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 661
2024-12-18 | 19:02 | 21.9434 | 85.3789 | 10.12 | 10.12 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 662
2024-12-18 | 19:02 | 21.9434 | 85.3789 | 33.45 | 156.12 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 663
2024-12-18 | 19:02 | 21.9434 | 85.3789 | 30.73 | 126.06 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 664
2024-12-18 | 19:02 | 21.9434 | 85.3789 | 36.16 | 183.49 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 665
2024-12-18 | 19:02 | 21.9434 | 85.3789 | 87.87 | 384.51 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 666
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 74.25 | 320.95 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 667
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 169.8 | 526.22 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 668
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 354.09 | 484.43 | 5 | ROC L8 KH-1 PIT-2 (CABIN) | 0 | 669
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 76.97 | 172.54 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 670
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 26.31 | 112.41 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 671
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 79.7 | 197.19 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 672
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 136.99 | 315.43 | 5 | ROC L8 KH-1 PIT-2 (CABIN) | 0 | 673
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 18.36 | 10.12 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 674
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 1.39 | 1.39 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 675
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 0 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 676
2024-12-18 | 19:03 | 21.9434 | 85.3788 | 0 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 10.3135 | 677
2024-12-18 | 19:03 | 21.9434 | 85.3788 | 0 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 678
2024-12-18 | 19:03 | 21.9434 | 85.3788 | 21.12 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 679
2024-12-18 | 19:03 | 21.9434 | 85.3788 | 18.36 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 680
2024-12-18 | 19:03 | 21.9434 | 85.3788 | 18.36 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 681
2024-12-18 | 19:03 | 21.9434 | 85.3788 | 21.12 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 682
2024-12-18 | 19:03 | 21.9434 | 85.3788 | 15.57 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 683
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 0 | 1.39 | 2.1 | ROC L8 KH-1 PIT-2 | 10.3135 | 684
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 3.16 | 18.36 | 2.2 | ROC L8 KH-1 PIT-2 (HOLE) | 0 | 685
2024-12-18 | 19:03 | 21.9434 | 85.3788 | 5.24 | 7.58 | 2.2 | ROC L8 KH-1 PIT-2 (HOLE) | 10.3135 | 686
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 210.9 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 10.3135 | 687
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 0 | 1.39 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 688
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 93.32 | 1.39 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 689
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 298.89 | 10.12 | 5 | ROC L8 KH-1 PIT-2 (CABIN) | 0 | 690
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 540.17 | 5.24 | 5 | ROC L8 KH-1 PIT-2 (CABIN) | 0 | 691
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 470.52 | 5.24 | 5 | ROC L8 KH-1 PIT-2 (CABIN) | 0 | 692
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 409.44 | 3.16 | 5 | ROC L8 KH-1 PIT-2 (CABIN) | 0 | 693
2024-12-18 | 19:03 | 21.9434 | 85.3789 | 312.67 | 3.16 | 5 | ROC L8 KH-1 PIT-2 (CABIN) | 0 | 694
2024-12-18 | 19:04 | 21.9434 | 85.3789 | 428.86 | 5.24 | 5 | ROC L8 KH-1 PIT-2 (CABIN) | 0 | 695
2024-12-18 | 19:04 | 21.9434 | 85.3789 | 390.05 | 18.36 | 5 | ROC L8 KH-1 PIT-2 (CABIN) | 0 | 696
2024-12-18 | 19:04 | 21.9434 | 85.3789 | 71.53 | 1.39 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 697
2024-12-18 | 19:04 | 21.9434 | 85.3789 | 1.39 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 698
2024-12-18 | 19:04 | 21.9434 | 85.3789 | 0 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 699
2024-12-18 | 19:04 | 21.9434 | 85.3789 | 10.12 | 5.24 | 2.2 | ROC L8 KH-1 PIT-2 (HOLE) | 0 | 700
2024-12-18 | 19:04 | 21.9433 | 85.3788 | 10.12 | 82.42 | 2.1 | ROC L8 KH-1 PIT-2 | 15.1662 | 701
2024-12-18 | 19:04 | 21.9433 | 85.3788 | 21.12 | 126.06 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 702
2024-12-18 | 19:04 | 21.9433 | 85.3788 | 3.16 | 112.41 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 703
2024-12-18 | 19:04 | 21.9433 | 85.3788 | 18.36 | 126.06 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 704
2024-12-18 | 19:04 | 21.9433 | 85.3788 | 15.57 | 109.68 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 705
2024-12-18 | 19:04 | 21.9433 | 85.3788 | 23.79 | 142.45 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 706
2024-12-18 | 19:06 | 21.9439 | 85.3788 | 87.87 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 66.7169 | 707
2024-12-18 | 19:06 | 21.9439 | 85.3788 | 87.87 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 708
2024-12-18 | 19:06 | 21.9439 | 85.3788 | 87.87 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 709
2024-12-18 | 19:06 | 21.9439 | 85.3788 | 87.87 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 710
2024-12-18 | 19:06 | 21.9439 | 85.3788 | 87.87 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 711
2024-12-18 | 19:06 | 21.9439 | 85.3788 | 87.87 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 712
2024-12-18 | 19:06 | 21.9439 | 85.3788 | 87.87 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 713
2024-12-18 | 19:06 | 21.9439 | 85.3788 | 87.87 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 714
2024-12-18 | 19:07 | 21.9439 | 85.3788 | 87.87 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 715
2024-12-18 | 19:07 | 21.944 | 85.3788 | 87.87 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 11.1192 | 716
2024-12-18 | 19:07 | 21.944 | 85.3788 | 90.59 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 717
2024-12-18 | 19:07 | 21.944 | 85.3788 | 90.59 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 718
2024-12-18 | 19:07 | 21.944 | 85.3788 | 90.59 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 719
2024-12-18 | 19:07 | 21.944 | 85.3788 | 90.59 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 720
2024-12-18 | 19:07 | 21.944 | 85.3788 | 90.59 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 721
2024-12-18 | 19:07 | 21.944 | 85.3788 | 90.59 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 722
2024-12-18 | 19:07 | 21.944 | 85.3788 | 90.59 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 723
2024-12-18 | 19:07 | 21.944 | 85.3788 | 90.59 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 724
2024-12-18 | 19:07 | 21.944 | 85.3788 | 90.59 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 725
2024-12-18 | 19:07 | 21.944 | 85.3788 | 90.59 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 726
2024-12-18 | 19:07 | 21.944 | 85.3788 | 90.59 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 727
2024-12-18 | 19:07 | 21.944 | 85.3788 | 90.59 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 728
2024-12-18 | 19:07 | 21.944 | 85.3788 | 93.32 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 729
2024-12-18 | 19:07 | 21.944 | 85.3788 | 98.77 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 730
2024-12-18 | 19:07 | 21.944 | 85.3788 | 139.72 | 0 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 731
2024-12-18 | 19:07 | 21.944 | 85.3788 | 323.71 | 1.39 | 2.1 | ROC L8 KH-1 PIT-2 | 0 | 732
2024-12-18 | 19:07 | 21.9441 | 85.3788 | 47.04 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 733
2024-12-18 | 19:07 | 21.9441 | 85.3788 | 7.58 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 734
2024-12-18 | 19:07 | 21.9441 | 85.3788 | 1.39 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 735
2024-12-18 | 19:07 | 21.9442 | 85.3788 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 736
2024-12-18 | 19:07 | 21.9442 | 85.3788 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 737
2024-12-18 | 19:07 | 21.9442 | 85.3788 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 738
2024-12-18 | 19:07 | 21.9443 | 85.3787 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1668 | 739
2024-12-18 | 19:07 | 21.9443 | 85.3787 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0.094935 | 740
2024-12-18 | 19:07 | 21.9443 | 85.3787 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0.094935 | 741
2024-12-18 | 19:07 | 21.9444 | 85.3786 | 0 | 3.16 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 742
2024-12-18 | 19:07 | 21.9444 | 85.3786 | 0 | 5.24 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 743
2024-12-18 | 19:07 | 21.9444 | 85.3786 | 0 | 3.16 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 744
2024-12-18 | 19:08 | 21.9445 | 85.3786 | 0 | 3.16 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 745
2024-12-18 | 19:08 | 21.9445 | 85.3785 | 0 | 3.16 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 746
2024-12-18 | 19:08 | 21.9445 | 85.3785 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 747
2024-12-18 | 19:08 | 21.9446 | 85.3785 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 748
2024-12-18 | 19:08 | 21.9446 | 85.3785 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 749
2024-12-18 | 19:08 | 21.9447 | 85.3785 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 750
2024-12-18 | 19:08 | 21.9447 | 85.3786 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 751
2024-12-18 | 19:08 | 21.9448 | 85.3786 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 752
2024-12-18 | 19:08 | 21.9448 | 85.3787 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 753
2024-12-18 | 19:08 | 21.9449 | 85.3788 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 754
2024-12-18 | 19:08 | 21.9449 | 85.3789 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 755
2024-12-18 | 19:08 | 21.9449 | 85.379 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 756
2024-12-18 | 19:08 | 21.945 | 85.379 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 757
2024-12-18 | 19:08 | 21.945 | 85.3791 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 758
2024-12-18 | 19:08 | 21.945 | 85.3792 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 759
2024-12-18 | 19:08 | 21.9451 | 85.3793 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 760
2024-12-18 | 19:08 | 21.9451 | 85.3794 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 761
2024-12-18 | 19:08 | 21.9451 | 85.3794 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 762
2024-12-18 | 19:08 | 21.9451 | 85.3795 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 763
2024-12-18 | 19:08 | 21.9452 | 85.3796 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1662 | 764
2024-12-18 | 19:08 | 21.9452 | 85.3797 | 5.24 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 765
2024-12-18 | 19:08 | 21.9452 | 85.3797 | 5.24 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 766
2024-12-18 | 19:08 | 21.9453 | 85.3798 | 10.12 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1662 | 767
2024-12-18 | 19:08 | 21.9453 | 85.3798 | 3.16 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 768
2024-12-18 | 19:08 | 21.9453 | 85.3799 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 769
2024-12-18 | 19:08 | 21.9454 | 85.3799 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 770
2024-12-18 | 19:08 | 21.9454 | 85.3799 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 771
2024-12-18 | 19:08 | 21.9455 | 85.3799 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 772
2024-12-18 | 19:08 | 21.9456 | 85.38 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 773
2024-12-18 | 19:08 | 21.9457 | 85.38 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 774
2024-12-18 | 19:09 | 21.9458 | 85.38 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 775
2024-12-18 | 19:09 | 21.9459 | 85.38 | 0 | 10.12 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 776
2024-12-18 | 19:09 | 21.946 | 85.3801 | 23.79 | 36.16 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 777
2024-12-18 | 19:09 | 21.9461 | 85.3801 | 82.42 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 778
2024-12-18 | 19:09 | 21.9462 | 85.3801 | 30.73 | 30.73 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 779
2024-12-18 | 19:09 | 21.9463 | 85.3801 | 49.76 | 10.12 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.12 | 780
2024-12-18 | 19:09 | 21.9464 | 85.3801 | 41.6 | 21.12 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 781
2024-12-18 | 19:09 | 21.9465 | 85.3802 | 36.16 | 18.36 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 782
2024-12-18 | 19:09 | 21.9466 | 85.3802 | 98.77 | 33.45 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 783
2024-12-18 | 19:09 | 21.9467 | 85.3802 | 49.76 | 33.45 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 784
2024-12-18 | 19:09 | 21.9468 | 85.3803 | 98.77 | 30.73 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 785
2024-12-18 | 19:09 | 21.9469 | 85.3803 | 49.76 | 30.73 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 786
2024-12-18 | 19:09 | 21.947 | 85.3804 | 79.7 | 21.12 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 787
2024-12-18 | 19:09 | 21.9471 | 85.3805 | 38.88 | 7.58 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 788
2024-12-18 | 19:09 | 21.9471 | 85.3806 | 79.7 | 49.76 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 789
2024-12-18 | 19:09 | 21.9471 | 85.3808 | 52.48 | 26.31 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 20.6274 | 790
2024-12-18 | 19:09 | 21.9472 | 85.3809 | 71.53 | 15.57 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 791
2024-12-18 | 19:09 | 21.9472 | 85.381 | 41.6 | 38.88 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 792
2024-12-18 | 19:09 | 21.9473 | 85.3811 | 74.25 | 5.24 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 793
2024-12-18 | 19:09 | 21.9473 | 85.3812 | 74.25 | 82.42 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3144 | 794
2024-12-18 | 19:09 | 21.9473 | 85.3814 | 101.5 | 7.58 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 20.6274 | 795
2024-12-18 | 19:09 | 21.9473 | 85.3815 | 126.06 | 30.73 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3144 | 796
2024-12-18 | 19:09 | 21.9474 | 85.3816 | 66.08 | 74.25 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 797
2024-12-18 | 19:09 | 21.9474 | 85.3817 | 161.59 | 5.24 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 798
2024-12-18 | 19:09 | 21.9474 | 85.3818 | 76.97 | 71.53 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 799
2024-12-18 | 19:09 | 21.9474 | 85.3819 | 139.72 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 800
2024-12-18 | 19:09 | 21.9475 | 85.382 | 12.8 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 801
2024-12-18 | 19:09 | 21.9475 | 85.3821 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 802
2024-12-18 | 19:09 | 21.9475 | 85.3822 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 803
2024-12-18 | 19:09 | 21.9475 | 85.3823 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 804
2024-12-18 | 19:10 | 21.9476 | 85.3824 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 805
2024-12-18 | 19:10 | 21.9476 | 85.3825 | 0 | 3.16 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 806
2024-12-18 | 19:10 | 21.9477 | 85.3825 | 0 | 3.16 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 807
2024-12-18 | 19:10 | 21.9478 | 85.3826 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 808
2024-12-18 | 19:10 | 21.9478 | 85.3827 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 809
2024-12-18 | 19:10 | 21.9479 | 85.3828 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1662 | 810
2024-12-18 | 19:10 | 21.948 | 85.3829 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 811
2024-12-18 | 19:10 | 21.9481 | 85.383 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1662 | 812
2024-12-18 | 19:10 | 21.9482 | 85.383 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 813
2024-12-18 | 19:10 | 21.9482 | 85.3831 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 814
2024-12-18 | 19:10 | 21.9483 | 85.3832 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 815
2024-12-18 | 19:10 | 21.9484 | 85.3833 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1662 | 816
2024-12-18 | 19:10 | 21.9485 | 85.3834 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 817
2024-12-18 | 19:10 | 21.9485 | 85.3835 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 818
2024-12-18 | 19:10 | 21.9486 | 85.3836 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1662 | 819
2024-12-18 | 19:10 | 21.9487 | 85.3837 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 820
2024-12-18 | 19:10 | 21.9488 | 85.3838 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1662 | 821
2024-12-18 | 19:10 | 21.9488 | 85.3839 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.313 | 822
2024-12-18 | 19:10 | 21.9489 | 85.384 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 823
2024-12-18 | 19:10 | 21.9489 | 85.3841 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 824
2024-12-18 | 19:10 | 21.949 | 85.3843 | 0 | 3.16 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 23.4333 | 825
2024-12-18 | 19:10 | 21.949 | 85.3844 | 5.24 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 826
2024-12-18 | 19:10 | 21.9491 | 85.3845 | 5.24 | 3.16 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1662 | 827
2024-12-18 | 19:10 | 21.9491 | 85.3847 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 20.6272 | 828
2024-12-18 | 19:10 | 21.9492 | 85.3848 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1662 | 829
2024-12-18 | 19:10 | 21.9492 | 85.3849 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 830
2024-12-18 | 19:10 | 21.9492 | 85.385 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 831
2024-12-18 | 19:10 | 21.9493 | 85.3851 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 832
2024-12-18 | 19:10 | 21.9493 | 85.3853 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 20.627 | 833
2024-12-18 | 19:10 | 21.9494 | 85.3854 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 834
2024-12-18 | 19:11 | 21.9494 | 85.3855 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.313 | 835
2024-12-18 | 19:11 | 21.9495 | 85.3856 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 836
2024-12-18 | 19:11 | 21.9495 | 85.3856 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 837
2024-12-18 | 19:11 | 21.9495 | 85.3857 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 838
2024-12-18 | 19:11 | 21.9496 | 85.3857 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 839
2024-12-18 | 19:11 | 21.9496 | 85.3858 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 840
2024-12-18 | 19:11 | 21.9496 | 85.3858 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 841
2024-12-18 | 19:11 | 21.9496 | 85.3859 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 842
2024-12-18 | 19:11 | 21.9496 | 85.3859 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 843
2024-12-18 | 19:11 | 21.9496 | 85.386 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 844
2024-12-18 | 19:11 | 21.9496 | 85.3861 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 845
2024-12-18 | 19:11 | 21.9496 | 85.3862 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 846
2024-12-18 | 19:11 | 21.9495 | 85.3862 | 0 | 3.16 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 847
2024-12-18 | 19:11 | 21.9495 | 85.3862 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 848
2024-12-18 | 19:11 | 21.9495 | 85.3863 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 849
2024-12-18 | 19:11 | 21.9495 | 85.3863 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 850
2024-12-18 | 19:11 | 21.9495 | 85.3864 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 851
2024-12-18 | 19:11 | 21.9495 | 85.3865 | 0 | 3.16 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 852
2024-12-18 | 19:11 | 21.9496 | 85.3865 | 3.16 | 5.24 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 853
2024-12-18 | 19:11 | 21.9496 | 85.3866 | 12.8 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 854
2024-12-18 | 19:11 | 21.9497 | 85.3867 | 10.12 | 7.58 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 855
2024-12-18 | 19:11 | 21.9498 | 85.3867 | 26.31 | 5.24 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 856
2024-12-18 | 19:11 | 21.9499 | 85.3868 | 26.31 | 26.31 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1665 | 857
2024-12-18 | 19:11 | 21.9499 | 85.3869 | 63.36 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 858
2024-12-18 | 19:11 | 21.95 | 85.387 | 36.16 | 26.31 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1662 | 859
2024-12-18 | 19:11 | 21.9501 | 85.387 | 66.08 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 860
2024-12-18 | 19:11 | 21.9501 | 85.3871 | 26.31 | 18.36 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 861
2024-12-18 | 19:11 | 21.9502 | 85.3872 | 60.64 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1662 | 862
2024-12-18 | 19:11 | 21.9503 | 85.3872 | 15.57 | 10.12 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 863
2024-12-18 | 19:11 | 21.9504 | 85.3873 | 10.12 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1662 | 864
2024-12-18 | 19:12 | 21.9505 | 85.3873 | 10.12 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 865
2024-12-18 | 19:12 | 21.9505 | 85.3872 | 3.16 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3126 | 866
2024-12-18 | 19:12 | 21.9506 | 85.3871 | 12.8 | 7.58 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 867
2024-12-18 | 19:12 | 21.9506 | 85.3871 | 55.2 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 868
2024-12-18 | 19:12 | 21.9507 | 85.387 | 26.31 | 21.12 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 869
2024-12-18 | 19:12 | 21.9507 | 85.3869 | 93.32 | 18.36 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 870
2024-12-18 | 19:12 | 21.9508 | 85.3868 | 26.31 | 5.24 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1662 | 871
2024-12-18 | 19:12 | 21.9508 | 85.3867 | 30.73 | 23.79 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.313 | 872
2024-12-18 | 19:12 | 21.9508 | 85.3866 | 41.6 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.313 | 873
2024-12-18 | 19:12 | 21.9509 | 85.3865 | 41.6 | 33.45 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 874
2024-12-18 | 19:12 | 21.9509 | 85.3864 | 87.87 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3139 | 875
2024-12-18 | 19:12 | 21.951 | 85.3863 | 23.79 | 21.12 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1662 | 876
2024-12-18 | 19:12 | 21.9511 | 85.3863 | 68.8 | 7.58 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 877
2024-12-18 | 19:12 | 21.9512 | 85.3862 | 33.45 | 26.31 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1662 | 878
2024-12-18 | 19:12 | 21.9512 | 85.3862 | 96.05 | 10.12 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 879
2024-12-18 | 19:12 | 21.9513 | 85.3862 | 18.36 | 23.79 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 880
2024-12-18 | 19:12 | 21.9514 | 85.3862 | 63.36 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 881
2024-12-18 | 19:12 | 21.9515 | 85.3862 | 12.8 | 12.8 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 882
2024-12-18 | 19:12 | 21.9516 | 85.3863 | 21.12 | 5.24 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 883
2024-12-18 | 19:12 | 21.9517 | 85.3863 | 15.57 | 3.16 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.12 | 884
2024-12-18 | 19:12 | 21.9518 | 85.3863 | 5.24 | 10.12 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 885
2024-12-18 | 19:12 | 21.9519 | 85.3864 | 10.12 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 886
2024-12-18 | 19:12 | 21.952 | 85.3864 | 7.58 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 887
2024-12-18 | 19:12 | 21.9521 | 85.3864 | 1.39 | 7.58 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 888
2024-12-18 | 19:12 | 21.9522 | 85.3865 | 1.39 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 889
2024-12-18 | 19:12 | 21.9523 | 85.3865 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 890
2024-12-18 | 19:12 | 21.9524 | 85.3865 | 7.58 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 891
2024-12-18 | 19:12 | 21.9526 | 85.3865 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 22.2388 | 892
2024-12-18 | 19:12 | 21.9526 | 85.3865 | 3.16 | 7.58 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 893
2024-12-18 | 19:12 | 21.9527 | 85.3864 | 44.32 | 3.16 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 894
2024-12-18 | 19:13 | 21.9528 | 85.3864 | 3.16 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 895
2024-12-18 | 19:13 | 21.9528 | 85.3863 | 0 | 10.12 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 896
2024-12-18 | 19:13 | 21.9529 | 85.3862 | 1.39 | 10.12 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 897
2024-12-18 | 19:13 | 21.9529 | 85.3861 | 0 | 10.12 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 898
2024-12-18 | 19:13 | 21.9529 | 85.386 | 1.39 | 12.8 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 899
2024-12-18 | 19:13 | 21.953 | 85.3859 | 3.16 | 12.8 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 900
2024-12-18 | 19:13 | 21.953 | 85.3858 | 7.58 | 15.57 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 901
2024-12-18 | 19:13 | 21.953 | 85.3857 | 12.8 | 21.12 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 902
2024-12-18 | 19:13 | 21.9531 | 85.3857 | 21.12 | 7.58 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 903
2024-12-18 | 19:13 | 21.9531 | 85.3856 | 23.79 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 904
2024-12-18 | 19:13 | 21.9531 | 85.3855 | 10.12 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 905
2024-12-18 | 19:13 | 21.9531 | 85.3854 | 3.16 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 906
2024-12-18 | 19:13 | 21.9531 | 85.3853 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 907
2024-12-18 | 19:13 | 21.953 | 85.3853 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1196 | 908
2024-12-18 | 19:13 | 21.953 | 85.3852 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 909
2024-12-18 | 19:13 | 21.9529 | 85.3852 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 910
2024-12-18 | 19:13 | 21.9528 | 85.3851 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 911
2024-12-18 | 19:13 | 21.9528 | 85.3851 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 912
2024-12-18 | 19:13 | 21.9527 | 85.385 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 913
2024-12-18 | 19:13 | 21.9527 | 85.385 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 914
2024-12-18 | 19:13 | 21.9526 | 85.3849 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 915
2024-12-18 | 19:13 | 21.9526 | 85.3848 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.313 | 916
2024-12-18 | 19:13 | 21.9525 | 85.3848 | 0 | 3.16 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 917
2024-12-18 | 19:13 | 21.9525 | 85.3847 | 0 | 7.58 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 918
2024-12-18 | 19:13 | 21.9525 | 85.3846 | 0 | 5.24 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 919
2024-12-18 | 19:13 | 21.9525 | 85.3845 | 0 | 7.58 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 920
2024-12-18 | 19:13 | 21.9525 | 85.3845 | 0 | 10.12 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 921
2024-12-18 | 19:13 | 21.9525 | 85.3844 | 0 | 15.57 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 922
2024-12-18 | 19:13 | 21.9525 | 85.3843 | 0 | 15.57 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 923
2024-12-18 | 19:13 | 21.9525 | 85.3843 | 0 | 18.36 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 924
2024-12-18 | 19:14 | 21.9525 | 85.3842 | 0 | 21.12 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 925
2024-12-18 | 19:14 | 21.9525 | 85.3842 | 0 | 18.36 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 926
2024-12-18 | 19:14 | 21.9526 | 85.3841 | 1.39 | 12.8 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 15.1659 | 927
2024-12-18 | 19:14 | 21.9526 | 85.3841 | 0 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 928
2024-12-18 | 19:14 | 21.9526 | 85.384 | 0 | 5.24 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.313 | 929
2024-12-18 | 19:14 | 21.9526 | 85.384 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 930
2024-12-18 | 19:14 | 21.9526 | 85.3839 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.313 | 931
2024-12-18 | 19:14 | 21.9525 | 85.3839 | 1.39 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 11.1192 | 932
2024-12-18 | 19:14 | 21.9525 | 85.3839 | 1.39 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 933
2024-12-18 | 19:14 | 21.9525 | 85.3839 | 12.8 | 49.76 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 934
2024-12-18 | 19:14 | 21.9525 | 85.3839 | 30.73 | 66.08 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 935
2024-12-18 | 19:14 | 21.9525 | 85.384 | 23.79 | 1.39 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 936
2024-12-18 | 19:14 | 21.9525 | 85.384 | 10.12 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 937
2024-12-18 | 19:14 | 21.9525 | 85.3841 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 10.3135 | 938
2024-12-18 | 19:14 | 21.9525 | 85.3841 | 0 | 0 | 6 | HAUL ROAD (IM SECTION TO PIT-1) | 0 | 939
2024-12-18 | 19:14 | 21.9525 | 85.3842 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 940
2024-12-18 | 19:14 | 21.9525 | 85.3842 | 0 | 0 | 6 | HAUL ROAD | 0 | 941
2024-12-18 | 19:14 | 21.9525 | 85.3843 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 942
2024-12-18 | 19:14 | 21.9525 | 85.3844 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 943
2024-12-18 | 19:14 | 21.9525 | 85.3844 | 0 | 0 | 6 | HAUL ROAD | 0 | 944
2024-12-18 | 19:14 | 21.9525 | 85.3845 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 945
2024-12-18 | 19:14 | 21.9525 | 85.3845 | 0 | 0 | 6 | HAUL ROAD | 0 | 946
2024-12-18 | 19:14 | 21.9525 | 85.3846 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 947
2024-12-18 | 19:14 | 21.9526 | 85.3847 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 948
2024-12-18 | 19:14 | 21.9526 | 85.3847 | 0 | 0 | 6 | HAUL ROAD | 0 | 949
2024-12-18 | 19:14 | 21.9526 | 85.3848 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 950
2024-12-18 | 19:14 | 21.9526 | 85.3849 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 951
2024-12-18 | 19:14 | 21.9527 | 85.3849 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 952
2024-12-18 | 19:14 | 21.9527 | 85.385 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 953
2024-12-18 | 19:14 | 21.9528 | 85.385 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 954
2024-12-18 | 19:15 | 21.9528 | 85.385 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 955
2024-12-18 | 19:15 | 21.9529 | 85.3851 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 956
2024-12-18 | 19:15 | 21.9529 | 85.3851 | 0 | 0 | 6 | HAUL ROAD | 0 | 957
2024-12-18 | 19:15 | 21.953 | 85.3851 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 958
2024-12-18 | 19:15 | 21.953 | 85.3851 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 959
2024-12-18 | 19:15 | 21.9531 | 85.3852 | 0 | 1.39 | 6 | HAUL ROAD | 15.1662 | 960
2024-12-18 | 19:15 | 21.9531 | 85.3853 | 0 | 3.16 | 6 | HAUL ROAD | 10.3135 | 961
2024-12-18 | 19:15 | 21.9531 | 85.3853 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 962
2024-12-18 | 19:15 | 21.9531 | 85.3854 | 3.16 | 7.58 | 6 | HAUL ROAD | 10.3135 | 963
2024-12-18 | 19:15 | 21.9531 | 85.3855 | 3.16 | 10.12 | 6 | HAUL ROAD | 10.3135 | 964
2024-12-18 | 19:15 | 21.9531 | 85.3855 | 10.12 | 10.12 | 6 | HAUL ROAD | 0 | 965
2024-12-18 | 19:15 | 21.9531 | 85.3856 | 18.36 | 3.16 | 6 | HAUL ROAD | 10.3135 | 966
2024-12-18 | 19:15 | 21.9531 | 85.3857 | 26.31 | 1.39 | 6 | HAUL ROAD | 10.3135 | 967
2024-12-18 | 19:15 | 21.9531 | 85.3858 | 26.31 | 0 | 6 | HAUL ROAD | 10.3135 | 968
2024-12-18 | 19:15 | 21.9531 | 85.3858 | 18.36 | 0 | 6 | HAUL ROAD | 0 | 969
2024-12-18 | 19:15 | 21.953 | 85.3859 | 7.58 | 0 | 6 | HAUL ROAD | 15.1662 | 970
2024-12-18 | 19:15 | 21.953 | 85.386 | 7.58 | 1.39 | 6 | HAUL ROAD | 10.3135 | 971
2024-12-18 | 19:15 | 21.953 | 85.3861 | 5.24 | 3.16 | 6 | HAUL ROAD | 10.3135 | 972
2024-12-18 | 19:15 | 21.9529 | 85.3862 | 0 | 3.16 | 6 | HAUL ROAD | 15.1659 | 973
2024-12-18 | 19:15 | 21.9529 | 85.3863 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 974
2024-12-18 | 19:15 | 21.9529 | 85.3863 | 0 | 0 | 6 | HAUL ROAD | 0 | 975
2024-12-18 | 19:15 | 21.9528 | 85.3864 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 976
2024-12-18 | 19:15 | 21.9528 | 85.3865 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 977
2024-12-18 | 19:15 | 21.9527 | 85.3865 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 978
2024-12-18 | 19:15 | 21.9527 | 85.3865 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 979
2024-12-18 | 19:15 | 21.9526 | 85.3866 | 5.24 | 0 | 6 | HAUL ROAD | 15.1659 | 980
2024-12-18 | 19:15 | 21.9525 | 85.3866 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 981
2024-12-18 | 19:15 | 21.9525 | 85.3866 | 0 | 0 | 6 | HAUL ROAD | 0 | 982
2024-12-18 | 19:15 | 21.9524 | 85.3866 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 983
2024-12-18 | 19:15 | 21.9523 | 85.3865 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 984
2024-12-18 | 19:16 | 21.9522 | 85.3865 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 985
2024-12-18 | 19:16 | 21.9521 | 85.3865 | 0 | 1.39 | 6 | HAUL ROAD | 11.1192 | 986
2024-12-18 | 19:16 | 21.952 | 85.3864 | 0 | 1.39 | 6 | HAUL ROAD | 15.1662 | 987
2024-12-18 | 19:16 | 21.9519 | 85.3864 | 0 | 3.16 | 6 | HAUL ROAD | 11.1192 | 988
2024-12-18 | 19:16 | 21.9519 | 85.3864 | 3.16 | 0 | 6 | HAUL ROAD | 0 | 989
2024-12-18 | 19:16 | 21.9518 | 85.3863 | 1.39 | 3.16 | 6 | HAUL ROAD | 15.1659 | 990
2024-12-18 | 19:16 | 21.9517 | 85.3863 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 991
2024-12-18 | 19:16 | 21.9516 | 85.3863 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 992
2024-12-18 | 19:16 | 21.9515 | 85.3863 | 1.39 | 0 | 6 | HAUL ROAD | 11.1192 | 993
2024-12-18 | 19:16 | 21.9514 | 85.3864 | 0 | 0 | 6 | HAUL ROAD | 15.1662 | 994
2024-12-18 | 19:16 | 21.9514 | 85.3864 | 0 | 0 | 6 | HAUL ROAD | 0 | 995
2024-12-18 | 19:16 | 21.9513 | 85.3864 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 996
2024-12-18 | 19:16 | 21.9512 | 85.3865 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 997
2024-12-18 | 19:16 | 21.9511 | 85.3866 | 0 | 0 | 6 | HAUL ROAD | 15.1662 | 998
2024-12-18 | 19:16 | 21.9511 | 85.3867 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 999
2024-12-18 | 19:16 | 21.951 | 85.3868 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 1000
2024-12-18 | 19:16 | 21.951 | 85.3868 | 0 | 0 | 6 | HAUL ROAD | 0 | 1001
2024-12-18 | 19:16 | 21.9509 | 85.3869 | 0 | 0 | 6 | HAUL ROAD | 15.1662 | 1002
2024-12-18 | 19:16 | 21.9509 | 85.387 | 0 | 0 | 6 | HAUL ROAD | 10.3139 | 1003
2024-12-18 | 19:16 | 21.9508 | 85.3871 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 1004
2024-12-18 | 19:16 | 21.9508 | 85.3872 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 1005
2024-12-18 | 19:16 | 21.9508 | 85.3872 | 0 | 0 | 6 | HAUL ROAD | 0 | 1006
2024-12-18 | 19:16 | 21.9507 | 85.3873 | 0 | 0 | 6 | HAUL ROAD | 15.1662 | 1007
2024-12-18 | 19:16 | 21.9507 | 85.3874 | 0 | 0 | 6 | HAUL ROAD | 10.3139 | 1008
2024-12-18 | 19:16 | 21.9507 | 85.3874 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 1009
2024-12-18 | 19:16 | 21.9507 | 85.3875 | 0 | 0 | 6 | HAUL ROAD | 10.3139 | 1010
2024-12-18 | 19:16 | 21.9506 | 85.3875 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1011
2024-12-18 | 19:16 | 21.9506 | 85.3876 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 1012
2024-12-18 | 19:16 | 21.9506 | 85.3876 | 0 | 0 | 6 | HAUL ROAD | 0 | 1013
2024-12-18 | 19:16 | 21.9506 | 85.3877 | 0 | 1.39 | 6 | HAUL ROAD | 10.3135 | 1014
2024-12-18 | 19:17 | 21.9506 | 85.3877 | 0 | 0 | 6 | HAUL ROAD | 0 | 1015
2024-12-18 | 19:17 | 21.9506 | 85.3878 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 1016
2024-12-18 | 19:17 | 21.9506 | 85.3879 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 1017
2024-12-18 | 19:17 | 21.9506 | 85.3879 | 0 | 0 | 6 | HAUL ROAD | 0 | 1018
2024-12-18 | 19:17 | 21.9507 | 85.388 | 0 | 3.16 | 6 | HAUL ROAD | 15.1659 | 1019
2024-12-18 | 19:17 | 21.9507 | 85.388 | 0 | 3.16 | 6 | HAUL ROAD | 0.094935 | 1020
2024-12-18 | 19:17 | 21.9508 | 85.3881 | 0 | 3.16 | 6 | HAUL ROAD | 15.1662 | 1021
2024-12-18 | 19:17 | 21.9509 | 85.3881 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1022
2024-12-18 | 19:17 | 21.951 | 85.3881 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1023
2024-12-18 | 19:17 | 21.951 | 85.3881 | 0 | 0 | 6 | HAUL ROAD | 0 | 1024
2024-12-18 | 19:17 | 21.9511 | 85.3881 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1025
2024-12-18 | 19:17 | 21.9512 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 15.1662 | 1026
2024-12-18 | 19:17 | 21.9513 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1027
2024-12-18 | 19:17 | 21.9514 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1028
2024-12-18 | 19:17 | 21.9515 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1029
2024-12-18 | 19:17 | 21.9516 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1030
2024-12-18 | 19:17 | 21.9517 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 1031
2024-12-18 | 19:17 | 21.9517 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 0 | 1032
2024-12-18 | 19:17 | 21.9518 | 85.3881 | 0 | 0 | 6 | HAUL ROAD | 15.1662 | 1033
2024-12-18 | 19:17 | 21.9519 | 85.3881 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1034
2024-12-18 | 19:17 | 21.9519 | 85.3881 | 0 | 0 | 6 | HAUL ROAD | 0 | 1035
2024-12-18 | 19:17 | 21.952 | 85.388 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 1036
2024-12-18 | 19:17 | 21.9521 | 85.388 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1037
2024-12-18 | 19:17 | 21.9521 | 85.388 | 0 | 0 | 6 | HAUL ROAD | 0 | 1038
2024-12-18 | 19:17 | 21.9522 | 85.388 | 1.39 | 0 | 6 | HAUL ROAD | 11.1192 | 1039
2024-12-18 | 19:17 | 21.9522 | 85.388 | 0 | 0 | 6 | HAUL ROAD | 0 | 1040
2024-12-18 | 19:17 | 21.9523 | 85.388 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1041
2024-12-18 | 19:17 | 21.9523 | 85.388 | 0 | 0 | 6 | HAUL ROAD | 0 | 1042
2024-12-18 | 19:17 | 21.9524 | 85.388 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1043
2024-12-18 | 19:17 | 21.9524 | 85.388 | 0 | 0 | 6 | HAUL ROAD | 0 | 1044
2024-12-18 | 19:18 | 21.9525 | 85.388 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1045
2024-12-18 | 19:18 | 21.9526 | 85.388 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1046
2024-12-18 | 19:18 | 21.9526 | 85.388 | 0 | 0 | 6 | HAUL ROAD | 0 | 1047
2024-12-18 | 19:18 | 21.9527 | 85.3881 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 1048
2024-12-18 | 19:18 | 21.9527 | 85.3881 | 0 | 0 | 6 | HAUL ROAD | 0 | 1049
2024-12-18 | 19:18 | 21.9528 | 85.3881 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1050
2024-12-18 | 19:18 | 21.9529 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 1051
2024-12-18 | 19:18 | 21.9529 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 0 | 1052
2024-12-18 | 19:18 | 21.953 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1053
2024-12-18 | 19:18 | 21.9531 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1054
2024-12-18 | 19:18 | 21.9531 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 0 | 1055
2024-12-18 | 19:18 | 21.9532 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1056
2024-12-18 | 19:18 | 21.9533 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1057
2024-12-18 | 19:18 | 21.9533 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 0 | 1058
2024-12-18 | 19:18 | 21.9534 | 85.3883 | 0 | 0 | 6 | HAUL ROAD | 15.1662 | 1059
2024-12-18 | 19:18 | 21.9535 | 85.3883 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1060
2024-12-18 | 19:18 | 21.9535 | 85.3883 | 0 | 0 | 6 | HAUL ROAD | 0 | 1061
2024-12-18 | 19:18 | 21.9536 | 85.3883 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1062
2024-12-18 | 19:18 | 21.9537 | 85.3883 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1063
2024-12-18 | 19:18 | 21.9538 | 85.3883 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1064
2024-12-18 | 19:18 | 21.9539 | 85.3884 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 1065
2024-12-18 | 19:18 | 21.9539 | 85.3884 | 0 | 0 | 6 | HAUL ROAD | 0 | 1066
2024-12-18 | 19:18 | 21.954 | 85.3884 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1067
2024-12-18 | 19:18 | 21.9541 | 85.3884 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1068
2024-12-18 | 19:18 | 21.9542 | 85.3884 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1069
2024-12-18 | 19:18 | 21.9542 | 85.3884 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 1070
2024-12-18 | 19:18 | 21.9543 | 85.3885 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 1071
2024-12-18 | 19:18 | 21.9544 | 85.3885 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1072
2024-12-18 | 19:18 | 21.9544 | 85.3885 | 0 | 0 | 6 | HAUL ROAD | 0 | 1073
2024-12-18 | 19:18 | 21.9545 | 85.3885 | 0 | 1.39 | 6 | HAUL ROAD | 11.12 | 1074
2024-12-18 | 19:19 | 21.9546 | 85.3886 | 0 | 1.39 | 6 | HAUL ROAD | 15.1659 | 1075
2024-12-18 | 19:19 | 21.9546 | 85.3886 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 1076
2024-12-18 | 19:19 | 21.9547 | 85.3886 | 0 | 1.39 | 6 | HAUL ROAD | 11.1196 | 1077
2024-12-18 | 19:19 | 21.9548 | 85.3886 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1078
2024-12-18 | 19:19 | 21.9548 | 85.3886 | 0 | 0 | 6 | HAUL ROAD | 0 | 1079
2024-12-18 | 19:19 | 21.9549 | 85.3886 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1080
2024-12-18 | 19:19 | 21.955 | 85.3887 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 1081
2024-12-18 | 19:19 | 21.955 | 85.3887 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 1082
2024-12-18 | 19:19 | 21.9551 | 85.3887 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1083
2024-12-18 | 19:19 | 21.9552 | 85.3887 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 1084
2024-12-18 | 19:19 | 21.9552 | 85.3887 | 0 | 0 | 6 | HAUL ROAD | 0 | 1085
2024-12-18 | 19:19 | 21.9553 | 85.3887 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1086
2024-12-18 | 19:19 | 21.9553 | 85.3887 | 0 | 0 | 6 | HAUL ROAD | 0 | 1087
2024-12-18 | 19:19 | 21.9554 | 85.3887 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1088
2024-12-18 | 19:19 | 21.9554 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 1089
2024-12-18 | 19:19 | 21.9555 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1090
2024-12-18 | 19:19 | 21.9555 | 85.3888 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 1091
2024-12-18 | 19:19 | 21.9556 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1092
2024-12-18 | 19:19 | 21.9556 | 85.3888 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 1093
2024-12-18 | 19:19 | 21.9557 | 85.3888 | 0 | 3.16 | 6 | HAUL ROAD | 11.1192 | 1094
2024-12-18 | 19:19 | 21.9558 | 85.3888 | 0 | 7.58 | 6 | HAUL ROAD | 11.1196 | 1095
2024-12-18 | 19:19 | 21.9558 | 85.3888 | 0 | 15.57 | 6 | HAUL ROAD | 0 | 1096
2024-12-18 | 19:19 | 21.9558 | 85.3888 | 1.39 | 30.73 | 6 | HAUL ROAD | 0 | 1097
2024-12-18 | 19:19 | 21.9559 | 85.3888 | 3.16 | 38.88 | 6 | HAUL ROAD | 11.1192 | 1098
2024-12-18 | 19:19 | 21.9559 | 85.3888 | 7.58 | 49.76 | 6 | HAUL ROAD | 0 | 1099
2024-12-18 | 19:19 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1100
2024-12-18 | 19:19 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1101
2024-12-18 | 19:19 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1102
2024-12-18 | 19:19 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1103
2024-12-18 | 19:19 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1104
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1105
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1106
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1107
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1108
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1109
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1110
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1111
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1112
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1113
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1114
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1115
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1116
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1117
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1118
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1119
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1120
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1121
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1122
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1123
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1124
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1125
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1126
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1127
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1128
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1129
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1130
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1131
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1132
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1133
2024-12-18 | 19:20 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1134
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1135
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1136
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1137
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1138
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1139
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1140
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1141
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1142
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1143
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1144
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1145
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1146
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1147
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1148
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1149
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1150
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1151
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1152
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1153
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1154
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1155
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1156
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1157
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1158
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1159
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1160
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1161
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1162
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1163
2024-12-18 | 19:21 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1164
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1165
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1166
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1167
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1168
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1169
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1170
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1171
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1172
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1173
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1174
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1175
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1176
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1177
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1178
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1179
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1180
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1181
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1182
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1183
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1184
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1185
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1186
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1187
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1188
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1189
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1190
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1191
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1192
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1193
2024-12-18 | 19:22 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1194
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1195
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1196
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1197
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1198
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1199
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1200
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1201
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1202
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1203
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1204
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1205
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1206
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1207
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1208
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1209
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1210
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1211
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1212
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1213
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1214
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1215
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1216
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1217
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 55.2 | 6 | HAUL ROAD | 0 | 1218
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 7.58 | 55.2 | 6 | HAUL ROAD | 0 | 1219
2024-12-18 | 19:23 | 21.9559 | 85.3888 | 10.12 | 60.64 | 6 | HAUL ROAD | 0 | 1220
2024-12-18 | 19:23 | 21.9559 | 85.3889 | 36.16 | 74.25 | 1 | DUMPER 37 (PIT-1) | 10.3126 | 1221
2024-12-18 | 19:23 | 21.956 | 85.3888 | 71.53 | 104.23 | 6 | HAUL ROAD | 15.1659 | 1222
2024-12-18 | 19:23 | 21.956 | 85.3888 | 158.86 | 205.42 | 6 | HAUL ROAD | 0 | 1223
2024-12-18 | 19:23 | 21.956 | 85.3888 | 139.72 | 136.99 | 6 | HAUL ROAD | 0 | 1224
2024-12-18 | 19:24 | 21.956 | 85.3888 | 142.45 | 139.72 | 6 | HAUL ROAD | 0 | 1225
2024-12-18 | 19:24 | 21.956 | 85.3888 | 142.45 | 139.72 | 6 | HAUL ROAD | 0 | 1226
2024-12-18 | 19:24 | 21.956 | 85.3888 | 142.45 | 142.45 | 6 | HAUL ROAD | 0 | 1227
2024-12-18 | 19:24 | 21.956 | 85.3888 | 142.45 | 142.45 | 6 | HAUL ROAD | 0 | 1228
2024-12-18 | 19:24 | 21.956 | 85.3888 | 142.45 | 142.45 | 6 | HAUL ROAD | 0 | 1229
2024-12-18 | 19:24 | 21.956 | 85.3888 | 142.45 | 142.45 | 6 | HAUL ROAD | 0 | 1230
2024-12-18 | 19:24 | 21.956 | 85.3888 | 145.18 | 136.99 | 6 | HAUL ROAD | 0 | 1231
2024-12-18 | 19:24 | 21.956 | 85.3888 | 134.25 | 147.92 | 6 | HAUL ROAD | 0 | 1232
2024-12-18 | 19:24 | 21.956 | 85.3888 | 66.08 | 183.49 | 6 | HAUL ROAD | 0 | 1233
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 0 | 90.59 | 6 | HAUL ROAD | 32.8764 | 1234
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 1.39 | 104.23 | 6 | HAUL ROAD | 0 | 1235
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 0 | 87.87 | 6 | HAUL ROAD | 0 | 1236
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 1.39 | 52.48 | 6 | HAUL ROAD | 0 | 1237
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 3.16 | 57.92 | 6 | HAUL ROAD | 0 | 1238
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 0 | 74.25 | 6 | HAUL ROAD | 0 | 1239
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 10.12 | 85.14 | 6 | HAUL ROAD | 0 | 1240
2024-12-18 | 19:25 | 21.9561 | 85.3884 | 0 | 98.77 | 6 | HAUL ROAD | 10.3126 | 1241
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 0 | 109.68 | 6 | HAUL ROAD | 10.3126 | 1242
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 1.39 | 33.45 | 6 | HAUL ROAD | 0 | 1243
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 1.39 | 82.42 | 6 | HAUL ROAD | 0 | 1244
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 15.57 | 85.14 | 6 | HAUL ROAD | 0 | 1245
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 0 | 104.23 | 6 | HAUL ROAD | 0 | 1246
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 0 | 85.14 | 6 | HAUL ROAD | 0 | 1247
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 0 | 60.64 | 6 | HAUL ROAD | 0 | 1248
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 3.16 | 33.45 | 6 | HAUL ROAD | 0 | 1249
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 3.16 | 60.64 | 6 | HAUL ROAD | 0 | 1250
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 0 | 52.48 | 6 | HAUL ROAD | 0 | 1251
2024-12-18 | 19:25 | 21.9561 | 85.3885 | 1.39 | 52.48 | 6 | HAUL ROAD | 0 | 1252
2024-12-18 | 19:27 | 21.9564 | 85.3886 | 3.16 | 93.32 | 1 | E579 SHOVEL (PIT-1) | 34.9163 | 1253
2024-12-18 | 19:27 | 21.9564 | 85.3886 | 3.16 | 93.32 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1254
2024-12-18 | 19:27 | 21.9564 | 85.3886 | 5.24 | 98.77 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1255
2024-12-18 | 19:27 | 21.9564 | 85.3886 | 10.12 | 96.05 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1256
2024-12-18 | 19:27 | 21.9564 | 85.3886 | 15.57 | 82.42 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1257
2024-12-18 | 19:27 | 21.9564 | 85.3886 | 23.79 | 109.68 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1258
2024-12-18 | 19:27 | 21.9564 | 85.3886 | 21.12 | 66.08 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1259
2024-12-18 | 19:27 | 21.9564 | 85.3886 | 26.31 | 150.65 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1260
2024-12-18 | 19:27 | 21.9564 | 85.3886 | 23.79 | 128.79 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1261
2024-12-18 | 19:27 | 21.9564 | 85.3886 | 12.8 | 47.04 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1262
2024-12-18 | 19:27 | 21.9564 | 85.3886 | 5.24 | 26.31 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1263
2024-12-18 | 19:27 | 21.9564 | 85.3886 | 5.24 | 60.64 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1264
2024-12-18 | 19:27 | 21.9564 | 85.3886 | 1.39 | 60.64 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1265
2024-12-18 | 19:27 | 21.9564 | 85.3886 | 7.58 | 38.88 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1266
2024-12-18 | 19:28 | 21.9564 | 85.3886 | 0 | 0 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1267
2024-12-18 | 19:28 | 21.9564 | 85.3886 | 0 | 0 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1268
2024-12-18 | 19:28 | 21.9564 | 85.3886 | 0 | 0 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1269
2024-12-18 | 19:28 | 21.9564 | 85.3886 | 0 | 0 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1270
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 0 | 0 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1271
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 0 | 0 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1272
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 0 | 1.39 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1273
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 0 | 0 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1274
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 21.12 | 18.36 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1275
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 63.36 | 10.12 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1276
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 38.88 | 5.24 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1277
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 71.53 | 0 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1278
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 202.68 | 0 | 5 | E579 SHOVEL (PIT-1) (CABIN) | 0.13426 | 1279
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 90.59 | 3.16 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1280
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 145.18 | 0 | 5 | E579 SHOVEL (PIT-1) (CABIN) | 0.13426 | 1281
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 120.6 | 0 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1282
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 329.23 | 10.12 | 5 | E579 SHOVEL (PIT-1) (CABIN) | 0.13426 | 1283
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 221.88 | 18.36 | 5 | E579 SHOVEL (PIT-1) (CABIN) | 0.13426 | 1284
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 0 | 10.12 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1285
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 0 | 10.12 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1286
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 0 | 10.12 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1287
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 0 | 12.8 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1288
2024-12-18 | 19:29 | 21.9564 | 85.3886 | 0 | 0 | 1 | E579 SHOVEL (PIT-1) | 0.13426 | 1289
2024-12-18 | 19:29 | 21.9563 | 85.3886 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 1290
2024-12-18 | 19:31 | 21.956 | 85.3888 | 120.6 | 120.6 | 6 | HAUL ROAD | 39.2202 | 1291
2024-12-18 | 19:31 | 21.956 | 85.3888 | 120.6 | 120.6 | 6 | HAUL ROAD | 0 | 1292
2024-12-18 | 19:31 | 21.956 | 85.3888 | 123.33 | 120.6 | 6 | HAUL ROAD | 0 | 1293
2024-12-18 | 19:31 | 21.956 | 85.3888 | 120.6 | 120.6 | 6 | HAUL ROAD | 0 | 1294
2024-12-18 | 19:31 | 21.956 | 85.3888 | 120.6 | 120.6 | 6 | HAUL ROAD | 0 | 1295
2024-12-18 | 19:32 | 21.956 | 85.3888 | 120.6 | 120.6 | 6 | HAUL ROAD | 0 | 1296
2024-12-18 | 19:32 | 21.956 | 85.3888 | 117.87 | 120.6 | 6 | HAUL ROAD | 0 | 1297
2024-12-18 | 19:32 | 21.956 | 85.3888 | 120.6 | 120.6 | 6 | HAUL ROAD | 0 | 1298
2024-12-18 | 19:32 | 21.956 | 85.3888 | 117.87 | 120.6 | 6 | HAUL ROAD | 0 | 1299
2024-12-18 | 19:32 | 21.956 | 85.3888 | 117.87 | 117.87 | 6 | HAUL ROAD | 0 | 1300
2024-12-18 | 19:32 | 21.956 | 85.3888 | 93.32 | 87.87 | 6 | HAUL ROAD | 0 | 1301
2024-12-18 | 19:32 | 21.956 | 85.3889 | 60.64 | 47.04 | 1 | DUMPER 37 (PIT-1) | 10.3126 | 1302
2024-12-18 | 19:32 | 21.956 | 85.3889 | 52.48 | 33.45 | 1 | DUMPER 37 (PIT-1) | 0 | 1303
2024-12-18 | 19:32 | 21.956 | 85.3888 | 55.2 | 26.31 | 6 | HAUL ROAD | 10.3126 | 1304
2024-12-18 | 19:32 | 21.956 | 85.3888 | 44.32 | 0 | 6 | HAUL ROAD | 0 | 1305
2024-12-18 | 19:32 | 21.9559 | 85.3888 | 23.79 | 0 | 6 | HAUL ROAD | 11.1192 | 1306
2024-12-18 | 19:32 | 21.9559 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 0 | 1307
2024-12-18 | 19:32 | 21.9559 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 0 | 1308
2024-12-18 | 19:32 | 21.9558 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1309
2024-12-18 | 19:32 | 21.9558 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 0 | 1310
2024-12-18 | 19:32 | 21.9557 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1311
2024-12-18 | 19:32 | 21.9557 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 0 | 1312
2024-12-18 | 19:32 | 21.9557 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 0 | 1313
2024-12-18 | 19:32 | 21.9556 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1314
2024-12-18 | 19:32 | 21.9556 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 0 | 1315
2024-12-18 | 19:32 | 21.9556 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 0 | 1316
2024-12-18 | 19:32 | 21.9555 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1317
2024-12-18 | 19:32 | 21.9555 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 0 | 1318
2024-12-18 | 19:32 | 21.9555 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 0 | 1319
2024-12-18 | 19:32 | 21.9554 | 85.3888 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 1320
2024-12-18 | 19:32 | 21.9554 | 85.3889 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 1321
2024-12-18 | 19:32 | 21.9554 | 85.3889 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 1322
2024-12-18 | 19:32 | 21.9553 | 85.389 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 1323
2024-12-18 | 19:32 | 21.9553 | 85.389 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 1324
2024-12-18 | 19:32 | 21.9553 | 85.3891 | 0 | 1.39 | 6 | HAUL ROAD | 10.3135 | 1325
2024-12-18 | 19:33 | 21.9554 | 85.3892 | 0 | 3.16 | 6 | HAUL ROAD | 15.1659 | 1326
2024-12-18 | 19:33 | 21.9554 | 85.3893 | 0 | 7.58 | 6 | HAUL ROAD | 10.3126 | 1327
2024-12-18 | 19:33 | 21.9554 | 85.3893 | 0 | 7.58 | 6 | HAUL ROAD | 0 | 1328
2024-12-18 | 19:33 | 21.9555 | 85.3894 | 0 | 1.39 | 6 | HAUL ROAD | 15.1659 | 1329
2024-12-18 | 19:33 | 21.9555 | 85.3895 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 1330
2024-12-18 | 19:33 | 21.9556 | 85.3895 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 1331
2024-12-18 | 19:33 | 21.9556 | 85.3896 | 0 | 1.39 | 6 | HAUL ROAD | 10.3126 | 1332
2024-12-18 | 19:33 | 21.9556 | 85.3896 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 1333
2024-12-18 | 19:33 | 21.9557 | 85.3897 | 0 | 3.16 | 6 | HAUL ROAD | 15.1659 | 1334
2024-12-18 | 19:33 | 21.9557 | 85.3897 | 0 | 10.12 | 6 | HAUL ROAD | 0 | 1335
2024-12-18 | 19:33 | 21.9558 | 85.3898 | 0 | 12.8 | 6 | HAUL ROAD | 15.1659 | 1336
2024-12-18 | 19:33 | 21.9558 | 85.3898 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 1337
2024-12-18 | 19:33 | 21.9559 | 85.3899 | 0 | 3.16 | 6 | HAUL ROAD | 15.1659 | 1338
2024-12-18 | 19:33 | 21.9559 | 85.3899 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 1339
2024-12-18 | 19:33 | 21.9559 | 85.3899 | 0 | 10.12 | 6 | HAUL ROAD | 0 | 1340
2024-12-18 | 19:33 | 21.9559 | 85.39 | 3.16 | 12.8 | 6 | HAUL ROAD | 10.3126 | 1341
2024-12-18 | 19:33 | 21.9559 | 85.39 | 5.24 | 10.12 | 6 | HAUL ROAD | 0 | 1342
2024-12-18 | 19:33 | 21.9559 | 85.39 | 63.36 | 7.58 | 6 | HAUL ROAD | 0 | 1343
2024-12-18 | 19:33 | 21.9558 | 85.39 | 843.89 | 7.58 | 5 | E571 SHOVEL (PIT-1) (CABIN) | 11.1192 | 1344
2024-12-18 | 19:33 | 21.9558 | 85.39 | 520.64 | 5.24 | 5 | E571 SHOVEL (PIT-1) (CABIN) | 0 | 1345
2024-12-18 | 19:33 | 21.9558 | 85.39 | 376.21 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1346
2024-12-18 | 19:33 | 21.9558 | 85.39 | 373.44 | 3.16 | 1 | E571 SHOVEL (PIT-1) | 0 | 1347
2024-12-18 | 19:33 | 21.9558 | 85.39 | 398.36 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1348
2024-12-18 | 19:33 | 21.9558 | 85.39 | 529.01 | 5.24 | 1 | E571 SHOVEL (PIT-1) | 0 | 1349
2024-12-18 | 19:33 | 21.9558 | 85.39 | 542.96 | 5.24 | 1 | E571 SHOVEL (PIT-1) | 0 | 1350
2024-12-18 | 19:33 | 21.9558 | 85.39 | 545.75 | 5.24 | 1 | E571 SHOVEL (PIT-1) | 0 | 1351
2024-12-18 | 19:33 | 21.9558 | 85.39 | 545.75 | 5.24 | 1 | E571 SHOVEL (PIT-1) | 0 | 1352
2024-12-18 | 19:33 | 21.9558 | 85.39 | 545.75 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1353
2024-12-18 | 19:33 | 21.9558 | 85.39 | 545.75 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1354
2024-12-18 | 19:33 | 21.9558 | 85.39 | 545.75 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1355
2024-12-18 | 19:34 | 21.9558 | 85.39 | 545.75 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1356
2024-12-18 | 19:34 | 21.9558 | 85.39 | 545.75 | 5.24 | 1 | E571 SHOVEL (PIT-1) | 0 | 1357
2024-12-18 | 19:34 | 21.9558 | 85.39 | 545.75 | 5.24 | 1 | E571 SHOVEL (PIT-1) | 0 | 1358
2024-12-18 | 19:34 | 21.9558 | 85.39 | 545.75 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1359
2024-12-18 | 19:34 | 21.9558 | 85.39 | 548.54 | 10.12 | 1 | E571 SHOVEL (PIT-1) | 0 | 1360
2024-12-18 | 19:34 | 21.9558 | 85.39 | 545.75 | 10.12 | 1 | E571 SHOVEL (PIT-1) | 0 | 1361
2024-12-18 | 19:34 | 21.9558 | 85.39 | 545.75 | 5.24 | 1 | E571 SHOVEL (PIT-1) | 0 | 1362
2024-12-18 | 19:34 | 21.9558 | 85.39 | 545.75 | 10.12 | 1 | E571 SHOVEL (PIT-1) | 0 | 1363
2024-12-18 | 19:34 | 21.9558 | 85.39 | 545.75 | 10.12 | 1 | E571 SHOVEL (PIT-1) | 0 | 1364
2024-12-18 | 19:34 | 21.9558 | 85.39 | 548.54 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1365
2024-12-18 | 19:34 | 21.9558 | 85.39 | 548.54 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1366
2024-12-18 | 19:34 | 21.9558 | 85.39 | 548.54 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1367
2024-12-18 | 19:34 | 21.9558 | 85.39 | 545.75 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1368
2024-12-18 | 19:34 | 21.9558 | 85.39 | 545.75 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1369
2024-12-18 | 19:34 | 21.9558 | 85.39 | 545.75 | 10.12 | 1 | E571 SHOVEL (PIT-1) | 0 | 1370
2024-12-18 | 19:34 | 21.9558 | 85.39 | 545.75 | 21.12 | 1 | E571 SHOVEL (PIT-1) | 0 | 1371
2024-12-18 | 19:34 | 21.9558 | 85.39 | 654.92 | 18.36 | 1 | E571 SHOVEL (PIT-1) | 0 | 1372
2024-12-18 | 19:34 | 21.9558 | 85.39 | 515.07 | 30.73 | 1 | E571 SHOVEL (PIT-1) | 0 | 1373
2024-12-18 | 19:34 | 21.9558 | 85.39 | 0 | 0 | 6 | HAUL ROAD | 0 | 1374
2024-12-18 | 19:34 | 21.9558 | 85.39 | 412.22 | 10.12 | 1 | E571 SHOVEL (PIT-1) | 0 | 1375
2024-12-18 | 19:34 | 21.9558 | 85.39 | 326.47 | 3.16 | 1 | E571 SHOVEL (PIT-1) | 0 | 1376
2024-12-18 | 19:34 | 21.9558 | 85.39 | 169.8 | 3.16 | 1 | E571 SHOVEL (PIT-1) | 0 | 1377
2024-12-18 | 19:34 | 21.9558 | 85.39 | 0 | 3.16 | 1 | E571 SHOVEL (PIT-1) | 0 | 1378
2024-12-18 | 19:34 | 21.9557 | 85.39 | 79.7 | 1.39 | 6 | HAUL ROAD | 11.1196 | 1379
2024-12-18 | 19:35 | 21.9557 | 85.3901 | 1.39 | 117.87 | 6 | HAUL ROAD | 10.313 | 1380
2024-12-18 | 19:35 | 21.9557 | 85.3901 | 10.12 | 123.33 | 6 | HAUL ROAD | 0 | 1381
2024-12-18 | 19:35 | 21.9557 | 85.39 | 0 | 136.99 | 6 | HAUL ROAD | 10.313 | 1382
2024-12-18 | 19:35 | 21.9557 | 85.39 | 12.8 | 180.75 | 6 | HAUL ROAD | 0 | 1383
2024-12-18 | 19:35 | 21.9557 | 85.39 | 30.73 | 150.65 | 6 | HAUL ROAD | 0 | 1384
2024-12-18 | 19:35 | 21.9557 | 85.39 | 21.12 | 82.42 | 6 | HAUL ROAD | 0 | 1385
2024-12-18 | 19:35 | 21.9557 | 85.39 | 7.58 | 202.68 | 6 | HAUL ROAD | 0 | 1386
2024-12-18 | 19:35 | 21.9557 | 85.3901 | 10.12 | 194.45 | 6 | HAUL ROAD | 10.313 | 1387
2024-12-18 | 19:36 | 21.9557 | 85.3901 | 5.24 | 178.02 | 6 | HAUL ROAD | 0 | 1388
2024-12-18 | 19:36 | 21.9557 | 85.3901 | 3.16 | 161.59 | 6 | HAUL ROAD | 0 | 1389
2024-12-18 | 19:36 | 21.9557 | 85.3901 | 12.8 | 134.25 | 6 | HAUL ROAD | 0 | 1390
2024-12-18 | 19:36 | 21.9557 | 85.3901 | 26.31 | 128.79 | 6 | HAUL ROAD | 0 | 1391
2024-12-18 | 19:36 | 21.9557 | 85.3901 | 10.12 | 120.6 | 6 | HAUL ROAD | 0 | 1392
2024-12-18 | 19:36 | 21.9557 | 85.3901 | 21.12 | 74.25 | 6 | HAUL ROAD | 0 | 1393
2024-12-18 | 19:36 | 21.9557 | 85.3901 | 26.31 | 38.88 | 6 | HAUL ROAD | 0 | 1394
2024-12-18 | 19:36 | 21.9557 | 85.3901 | 15.57 | 117.87 | 6 | HAUL ROAD | 0 | 1395
2024-12-18 | 19:37 | 21.9556 | 85.3901 | 285.11 | 156.12 | 5 | SHOVEL E-571 PIT-1 | 11.1192 | 1396
2024-12-18 | 19:38 | 21.9556 | 85.3901 | 312.67 | 0 | 5 | SHOVEL E-571 PIT-1 | 0 | 1397
2024-12-18 | 19:38 | 21.9556 | 85.3901 | 260.34 | 0 | 5 | SHOVEL E-571 PIT-1 | 0 | 1398
2024-12-18 | 19:38 | 21.9556 | 85.3901 | 147.92 | 12.8 | 5 | SHOVEL E-571 PIT-1 | 0 | 1399
2024-12-18 | 19:40 | 21.9558 | 85.39 | 534.58 | 12.8 | 1 | E571 SHOVEL (PIT-1) | 24.5139 | 1400
2024-12-18 | 19:40 | 21.9558 | 85.39 | 540.17 | 12.8 | 1 | E571 SHOVEL (PIT-1) | 0 | 1401
2024-12-18 | 19:40 | 21.9558 | 85.39 | 540.17 | 21.12 | 1 | E571 SHOVEL (PIT-1) | 0 | 1402
2024-12-18 | 19:40 | 21.9558 | 85.39 | 540.17 | 18.36 | 1 | E571 SHOVEL (PIT-1) | 0 | 1403
2024-12-18 | 19:40 | 21.9558 | 85.39 | 540.17 | 15.57 | 1 | E571 SHOVEL (PIT-1) | 0 | 1404
2024-12-18 | 19:40 | 21.9558 | 85.39 | 451.07 | 15.57 | 1 | E571 SHOVEL (PIT-1) | 0 | 1405
2024-12-18 | 19:40 | 21.9558 | 85.39 | 503.92 | 18.36 | 1 | E571 SHOVEL (PIT-1) | 0 | 1406
2024-12-18 | 19:40 | 21.9558 | 85.39 | 545.75 | 15.57 | 1 | E571 SHOVEL (PIT-1) | 0 | 1407
2024-12-18 | 19:40 | 21.9558 | 85.39 | 551.33 | 21.12 | 1 | E571 SHOVEL (PIT-1) | 0 | 1408
2024-12-18 | 19:40 | 21.9558 | 85.39 | 542.96 | 18.36 | 1 | E571 SHOVEL (PIT-1) | 0 | 1409
2024-12-18 | 19:40 | 21.9558 | 85.39 | 545.75 | 18.36 | 1 | E571 SHOVEL (PIT-1) | 0 | 1410
2024-12-18 | 19:40 | 21.9558 | 85.39 | 556.92 | 21.12 | 1 | E571 SHOVEL (PIT-1) | 0 | 1411
2024-12-18 | 19:40 | 21.9558 | 85.39 | 559.71 | 21.12 | 1 | E571 SHOVEL (PIT-1) | 0 | 1412
2024-12-18 | 19:40 | 21.9558 | 85.39 | 559.71 | 21.12 | 1 | E571 SHOVEL (PIT-1) | 0 | 1413
2024-12-18 | 19:40 | 21.9558 | 85.39 | 559.71 | 21.12 | 1 | E571 SHOVEL (PIT-1) | 0 | 1414
2024-12-18 | 19:40 | 21.9558 | 85.39 | 556.92 | 21.12 | 1 | E571 SHOVEL (PIT-1) | 0 | 1415
2024-12-18 | 19:40 | 21.9558 | 85.39 | 556.92 | 18.36 | 1 | E571 SHOVEL (PIT-1) | 0 | 1416
2024-12-18 | 19:40 | 21.9558 | 85.39 | 545.75 | 18.36 | 1 | E571 SHOVEL (PIT-1) | 0 | 1417
2024-12-18 | 19:40 | 21.9558 | 85.39 | 545.75 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1418
2024-12-18 | 19:41 | 21.9558 | 85.39 | 545.75 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1419
2024-12-18 | 19:41 | 21.9558 | 85.39 | 545.75 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1420
2024-12-18 | 19:41 | 21.9558 | 85.39 | 545.75 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1421
2024-12-18 | 19:41 | 21.9558 | 85.39 | 551.33 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1422
2024-12-18 | 19:41 | 21.9558 | 85.39 | 551.33 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1423
2024-12-18 | 19:41 | 21.9558 | 85.39 | 448.29 | 7.58 | 1 | E571 SHOVEL (PIT-1) | 0 | 1424
2024-12-18 | 19:41 | 21.9557 | 85.39 | 210.9 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1425
2024-12-18 | 19:41 | 21.9557 | 85.39 | 18.36 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1426
2024-12-18 | 19:41 | 21.9557 | 85.3899 | 0 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1427
2024-12-18 | 19:41 | 21.9557 | 85.3899 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1428
2024-12-18 | 19:41 | 21.9556 | 85.3898 | 0 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1429
2024-12-18 | 19:41 | 21.9556 | 85.3898 | 0 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1430
2024-12-18 | 19:41 | 21.9556 | 85.3897 | 0 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 10.3126 | 1431
2024-12-18 | 19:41 | 21.9555 | 85.3897 | 0 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1432
2024-12-18 | 19:41 | 21.9555 | 85.3896 | 0 | 10.12 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1433
2024-12-18 | 19:41 | 21.9554 | 85.3896 | 0 | 10.12 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1434
2024-12-18 | 19:41 | 21.9554 | 85.3896 | 0 | 10.12 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1435
2024-12-18 | 19:41 | 21.9553 | 85.3895 | 1.39 | 10.12 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1436
2024-12-18 | 19:41 | 21.9553 | 85.3895 | 0 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1437
2024-12-18 | 19:41 | 21.9553 | 85.3895 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1438
2024-12-18 | 19:41 | 21.9552 | 85.3895 | 3.16 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1439
2024-12-18 | 19:41 | 21.9552 | 85.3894 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1440
2024-12-18 | 19:41 | 21.9551 | 85.3894 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.12 | 1441
2024-12-18 | 19:41 | 21.9551 | 85.3893 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.3135 | 1442
2024-12-18 | 19:41 | 21.955 | 85.3893 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1443
2024-12-18 | 19:41 | 21.9549 | 85.3893 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1444
2024-12-18 | 19:41 | 21.9548 | 85.3893 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1445
2024-12-18 | 19:41 | 21.9548 | 85.3893 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1446
2024-12-18 | 19:41 | 21.9547 | 85.3893 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1447
2024-12-18 | 19:41 | 21.9546 | 85.3893 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1448
2024-12-18 | 19:42 | 21.9545 | 85.3893 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.12 | 1449
2024-12-18 | 19:42 | 21.9544 | 85.3893 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.12 | 1450
2024-12-18 | 19:42 | 21.9544 | 85.3893 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1451
2024-12-18 | 19:42 | 21.9543 | 85.3892 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1452
2024-12-18 | 19:42 | 21.9542 | 85.3892 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.12 | 1453
2024-12-18 | 19:42 | 21.9541 | 85.3893 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1454
2024-12-18 | 19:42 | 21.9541 | 85.3893 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1455
2024-12-18 | 19:42 | 21.954 | 85.3893 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1456
2024-12-18 | 19:42 | 21.9539 | 85.3894 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1457
2024-12-18 | 19:42 | 21.9539 | 85.3894 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1458
2024-12-18 | 19:42 | 21.9538 | 85.3894 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1459
2024-12-18 | 19:42 | 21.9537 | 85.3895 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1460
2024-12-18 | 19:42 | 21.9536 | 85.3896 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1461
2024-12-18 | 19:42 | 21.9536 | 85.3896 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1462
2024-12-18 | 19:42 | 21.9535 | 85.3896 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1463
2024-12-18 | 19:42 | 21.9534 | 85.3897 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1464
2024-12-18 | 19:42 | 21.9533 | 85.3897 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1465
2024-12-18 | 19:42 | 21.9532 | 85.3898 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1466
2024-12-18 | 19:42 | 21.9531 | 85.3898 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1467
2024-12-18 | 19:42 | 21.953 | 85.3897 | 0 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1468
2024-12-18 | 19:42 | 21.9529 | 85.3897 | 0 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1469
2024-12-18 | 19:42 | 21.9528 | 85.3897 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1470
2024-12-18 | 19:42 | 21.9527 | 85.3897 | 0 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1471
2024-12-18 | 19:42 | 21.9526 | 85.3897 | 68.8 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1472
2024-12-18 | 19:42 | 21.9525 | 85.3897 | 10.12 | 23.79 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1473
2024-12-18 | 19:42 | 21.9523 | 85.3897 | 10.12 | 10.12 | 6 | HAUL ROAD (PIT-1 16D) | 22.239 | 1474
2024-12-18 | 19:42 | 21.9522 | 85.3897 | 44.32 | 15.57 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1475
2024-12-18 | 19:42 | 21.9521 | 85.3896 | 10.12 | 38.88 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1476
2024-12-18 | 19:42 | 21.952 | 85.3896 | 134.25 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1477
2024-12-18 | 19:42 | 21.9519 | 85.3896 | 0 | 15.57 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1478
2024-12-18 | 19:43 | 21.9518 | 85.3896 | 23.79 | 23.79 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1479
2024-12-18 | 19:43 | 21.9517 | 85.3896 | 3.16 | 12.8 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1480
2024-12-18 | 19:43 | 21.9515 | 85.3895 | 21.12 | 7.58 | 6 | HAUL ROAD (PIT-1 16D) | 24.5141 | 1481
2024-12-18 | 19:43 | 21.9514 | 85.3895 | 12.8 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1482
2024-12-18 | 19:43 | 21.9513 | 85.3895 | 7.58 | 10.12 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1483
2024-12-18 | 19:43 | 21.9512 | 85.3894 | 12.8 | 10.12 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1484
2024-12-18 | 19:43 | 21.9511 | 85.3894 | 3.16 | 12.8 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1485
2024-12-18 | 19:43 | 21.951 | 85.3893 | 3.16 | 7.58 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1486
2024-12-18 | 19:43 | 21.9509 | 85.3893 | 0 | 12.8 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1487
2024-12-18 | 19:43 | 21.9508 | 85.3892 | 0 | 18.36 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1488
2024-12-18 | 19:43 | 21.9507 | 85.3892 | 1.39 | 15.57 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1489
2024-12-18 | 19:43 | 21.9506 | 85.3891 | 1.39 | 15.57 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1490
2024-12-18 | 19:43 | 21.9505 | 85.3891 | 0 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1491
2024-12-18 | 19:43 | 21.9505 | 85.389 | 1.39 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 10.3126 | 1492
2024-12-18 | 19:43 | 21.9504 | 85.389 | 1.39 | 7.58 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1493
2024-12-18 | 19:43 | 21.9504 | 85.389 | 5.24 | 23.79 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1494
2024-12-18 | 19:43 | 21.9503 | 85.3891 | 15.57 | 33.45 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1495
2024-12-18 | 19:43 | 21.9504 | 85.3892 | 18.36 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1496
2024-12-18 | 19:43 | 21.9504 | 85.3892 | 5.24 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1497
2024-12-18 | 19:43 | 21.9505 | 85.3893 | 1.39 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1498
2024-12-18 | 19:43 | 21.9506 | 85.3893 | 10.12 | 23.79 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1499
2024-12-18 | 19:43 | 21.9507 | 85.3894 | 15.57 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1500
2024-12-18 | 19:43 | 21.9508 | 85.3894 | 5.24 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1501
2024-12-18 | 19:43 | 21.9508 | 85.3895 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1502
2024-12-18 | 19:43 | 21.9509 | 85.3895 | 5.24 | 18.36 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1503
2024-12-18 | 19:43 | 21.951 | 85.3896 | 21.12 | 7.58 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1504
2024-12-18 | 19:43 | 21.9512 | 85.3896 | 21.12 | 7.58 | 6 | HAUL ROAD (PIT-1 16D) | 22.239 | 1505
2024-12-18 | 19:43 | 21.9512 | 85.3896 | 5.24 | 15.57 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1506
2024-12-18 | 19:43 | 21.9513 | 85.3897 | 23.79 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1507
2024-12-18 | 19:43 | 21.9515 | 85.3897 | 0 | 15.57 | 6 | HAUL ROAD (PIT-1 16D) | 22.239 | 1508
2024-12-18 | 19:44 | 21.9516 | 85.3897 | 36.16 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1509
2024-12-18 | 19:44 | 21.9517 | 85.3897 | 0 | 12.8 | 6 | HAUL ROAD (PIT-1 16D) | 11.12 | 1510
2024-12-18 | 19:44 | 21.9518 | 85.3897 | 134.25 | 10.12 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1511
2024-12-18 | 19:44 | 21.9519 | 85.3897 | 1.39 | 36.16 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1512
2024-12-18 | 19:44 | 21.952 | 85.3897 | 71.53 | 7.58 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1513
2024-12-18 | 19:44 | 21.9521 | 85.3898 | 0 | 7.58 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1514
2024-12-18 | 19:44 | 21.9522 | 85.3898 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1515
2024-12-18 | 19:44 | 21.9523 | 85.3898 | 0 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1516
2024-12-18 | 19:44 | 21.9524 | 85.3898 | 21.12 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1517
2024-12-18 | 19:44 | 21.9525 | 85.3898 | 3.16 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1518
2024-12-18 | 19:44 | 21.9526 | 85.3899 | 5.24 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1519
2024-12-18 | 19:44 | 21.9527 | 85.3899 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1520
2024-12-18 | 19:44 | 21.9528 | 85.39 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1521
2024-12-18 | 19:44 | 21.9529 | 85.39 | 1.39 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1522
2024-12-18 | 19:44 | 21.953 | 85.39 | 7.58 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1523
2024-12-18 | 19:44 | 21.9531 | 85.3901 | 5.24 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1524
2024-12-18 | 19:44 | 21.9532 | 85.3901 | 12.8 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1525
2024-12-18 | 19:44 | 21.9533 | 85.3902 | 12.8 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1526
2024-12-18 | 19:44 | 21.9534 | 85.3902 | 5.24 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1527
2024-12-18 | 19:44 | 21.9535 | 85.3903 | 18.36 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1528
2024-12-18 | 19:44 | 21.9536 | 85.3903 | 10.12 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1529
2024-12-18 | 19:44 | 21.9537 | 85.3904 | 5.24 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1530
2024-12-18 | 19:44 | 21.9538 | 85.3904 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1531
2024-12-18 | 19:44 | 21.9539 | 85.3904 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1532
2024-12-18 | 19:44 | 21.954 | 85.3905 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1533
2024-12-18 | 19:44 | 21.9542 | 85.3905 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 22.239 | 1534
2024-12-18 | 19:44 | 21.9543 | 85.3906 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1535
2024-12-18 | 19:44 | 21.9544 | 85.3906 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1536
2024-12-18 | 19:44 | 21.9545 | 85.3907 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1537
2024-12-18 | 19:44 | 21.9546 | 85.3907 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.12 | 1538
2024-12-18 | 19:45 | 21.9547 | 85.3908 | 0 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1539
2024-12-18 | 19:45 | 21.9548 | 85.3909 | 79.7 | 21.12 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1540
2024-12-18 | 19:45 | 21.9549 | 85.3909 | 60.64 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1541
2024-12-18 | 19:45 | 21.955 | 85.391 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1542
2024-12-18 | 19:45 | 21.9551 | 85.391 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1543
2024-12-18 | 19:45 | 21.9552 | 85.391 | 0 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 11.12 | 1544
2024-12-18 | 19:45 | 21.9553 | 85.3911 | 0 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1545
2024-12-18 | 19:45 | 21.9554 | 85.3912 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1546
2024-12-18 | 19:45 | 21.9555 | 85.3912 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1547
2024-12-18 | 19:45 | 21.9556 | 85.3913 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1548
2024-12-18 | 19:45 | 21.9557 | 85.3913 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1549
2024-12-18 | 19:45 | 21.9559 | 85.3914 | 0 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 24.5139 | 1550
2024-12-18 | 19:45 | 21.956 | 85.3914 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1551
2024-12-18 | 19:45 | 21.9561 | 85.3915 | 0 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1552
2024-12-18 | 19:45 | 21.9562 | 85.3915 | 3.16 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1553
2024-12-18 | 19:45 | 21.9563 | 85.3916 | 36.16 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1554
2024-12-18 | 19:45 | 21.9564 | 85.3916 | 12.8 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.12 | 1555
2024-12-18 | 19:45 | 21.9565 | 85.3917 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1556
2024-12-18 | 19:45 | 21.9566 | 85.3917 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1557
2024-12-18 | 19:45 | 21.9567 | 85.3917 | 1.39 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1558
2024-12-18 | 19:45 | 21.9568 | 85.3918 | 5.24 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1559
2024-12-18 | 19:45 | 21.9569 | 85.3918 | 7.58 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.12 | 1560
2024-12-18 | 19:45 | 21.957 | 85.3918 | 7.58 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 11.12 | 1561
2024-12-18 | 19:45 | 21.9571 | 85.3919 | 12.8 | 7.58 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1562
2024-12-18 | 19:45 | 21.9572 | 85.3919 | 18.36 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1563
2024-12-18 | 19:45 | 21.9573 | 85.3919 | 5.24 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1564
2024-12-18 | 19:45 | 21.9574 | 85.3919 | 3.16 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1565
2024-12-18 | 19:45 | 21.9575 | 85.3919 | 1.39 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1566
2024-12-18 | 19:45 | 21.9576 | 85.3919 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1567
2024-12-18 | 19:45 | 21.9577 | 85.3918 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1568
2024-12-18 | 19:46 | 21.9577 | 85.3917 | 0 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1569
2024-12-18 | 19:46 | 21.9577 | 85.3916 | 0 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1570
2024-12-18 | 19:46 | 21.9577 | 85.3915 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1571
2024-12-18 | 19:46 | 21.9577 | 85.3914 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1572
2024-12-18 | 19:46 | 21.9577 | 85.3913 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1573
2024-12-18 | 19:46 | 21.9577 | 85.3912 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1574
2024-12-18 | 19:46 | 21.9578 | 85.3911 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1575
2024-12-18 | 19:46 | 21.9578 | 85.391 | 0 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 10.3135 | 1576
2024-12-18 | 19:46 | 21.9579 | 85.391 | 0 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1577
2024-12-18 | 19:46 | 21.958 | 85.3909 | 3.16 | 10.12 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1578
2024-12-18 | 19:46 | 21.9581 | 85.391 | 5.24 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1579
2024-12-18 | 19:46 | 21.9582 | 85.391 | 5.24 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1580
2024-12-18 | 19:46 | 21.9583 | 85.3911 | 1.39 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1581
2024-12-18 | 19:46 | 21.9583 | 85.3912 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.3126 | 1582
2024-12-18 | 19:46 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1583
2024-12-18 | 19:46 | 21.9584 | 85.3914 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.3135 | 1584
2024-12-18 | 19:46 | 21.9584 | 85.3915 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.3135 | 1585
2024-12-18 | 19:46 | 21.9585 | 85.3916 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1586
2024-12-18 | 19:46 | 21.9585 | 85.3918 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 20.6257 | 1587
2024-12-18 | 19:46 | 21.9586 | 85.3919 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1588
2024-12-18 | 19:46 | 21.9586 | 85.392 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.3135 | 1589
2024-12-18 | 19:46 | 21.9587 | 85.3921 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1590
2024-12-18 | 19:46 | 21.9588 | 85.3921 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1591
2024-12-18 | 19:46 | 21.9588 | 85.3922 | 0 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 10.3126 | 1592
2024-12-18 | 19:46 | 21.9589 | 85.3923 | 0 | 7.58 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1593
2024-12-18 | 19:46 | 21.9589 | 85.3924 | 0 | 15.57 | 6 | HAUL ROAD (PIT-1 16D) | 10.3126 | 1594
2024-12-18 | 19:46 | 21.959 | 85.3925 | 5.24 | 21.12 | 6 | HAUL ROAD (PIT-1 16D) | 15.1656 | 1595
2024-12-18 | 19:46 | 21.959 | 85.3926 | 7.58 | 38.88 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1596
2024-12-18 | 19:46 | 21.959 | 85.3927 | 26.31 | 33.45 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1597
2024-12-18 | 19:46 | 21.9591 | 85.3928 | 23.79 | 12.8 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1598
2024-12-18 | 19:47 | 21.9591 | 85.3928 | 7.58 | 26.31 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1599
2024-12-18 | 19:47 | 21.9591 | 85.3929 | 44.32 | 41.6 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1600
2024-12-18 | 19:47 | 21.9591 | 85.3929 | 36.16 | 23.79 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1601
2024-12-18 | 19:47 | 21.9591 | 85.3929 | 23.79 | 38.88 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1602
2024-12-18 | 19:47 | 21.9591 | 85.3929 | 23.79 | 38.88 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1603
2024-12-18 | 19:47 | 21.9591 | 85.3929 | 15.57 | 68.8 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1604
2024-12-18 | 19:47 | 21.9591 | 85.3929 | 3.16 | 30.73 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1605
2024-12-18 | 19:47 | 21.9591 | 85.3929 | 7.58 | 26.31 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1606
2024-12-18 | 19:47 | 21.959 | 85.3929 | 5.24 | 49.76 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1607
2024-12-18 | 19:47 | 21.959 | 85.3928 | 15.57 | 60.64 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1608
2024-12-18 | 19:47 | 21.959 | 85.3927 | 18.36 | 18.36 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1609
2024-12-18 | 19:47 | 21.959 | 85.3927 | 23.79 | 10.12 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1610
2024-12-18 | 19:47 | 21.959 | 85.3926 | 21.12 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1611
2024-12-18 | 19:47 | 21.9589 | 85.3925 | 15.57 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1656 | 1612
2024-12-18 | 19:47 | 21.9589 | 85.3925 | 1.39 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 0 | 1613
2024-12-18 | 19:47 | 21.9589 | 85.3924 | 7.58 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.3126 | 1614
2024-12-18 | 19:47 | 21.9588 | 85.3923 | 1.39 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1615
2024-12-18 | 19:47 | 21.9588 | 85.3922 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.3126 | 1616
2024-12-18 | 19:47 | 21.9587 | 85.3922 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1617
2024-12-18 | 19:47 | 21.9587 | 85.3921 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.3135 | 1618
2024-12-18 | 19:47 | 21.9586 | 85.392 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1619
2024-12-18 | 19:47 | 21.9585 | 85.3919 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1620
2024-12-18 | 19:47 | 21.9585 | 85.3918 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.3135 | 1621
2024-12-18 | 19:47 | 21.9585 | 85.3916 | 0 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 20.6257 | 1622
2024-12-18 | 19:47 | 21.9584 | 85.3915 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1623
2024-12-18 | 19:47 | 21.9584 | 85.3914 | 0 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 10.3135 | 1624
2024-12-18 | 19:47 | 21.9584 | 85.3913 | 0 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 10.3135 | 1625
2024-12-18 | 19:47 | 21.9583 | 85.3912 | 0 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1626
2024-12-18 | 19:47 | 21.9583 | 85.3911 | 0 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 10.3126 | 1627
2024-12-18 | 19:47 | 21.9582 | 85.391 | 3.16 | 10.12 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1628
2024-12-18 | 19:48 | 21.9581 | 85.391 | 3.16 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1629
2024-12-18 | 19:48 | 21.958 | 85.391 | 1.39 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1630
2024-12-18 | 19:48 | 21.9579 | 85.391 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1631
2024-12-18 | 19:48 | 21.9578 | 85.3911 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1632
2024-12-18 | 19:48 | 21.9577 | 85.3912 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1633
2024-12-18 | 19:48 | 21.9577 | 85.3913 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1634
2024-12-18 | 19:48 | 21.9577 | 85.3915 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 20.6259 | 1635
2024-12-18 | 19:48 | 21.9577 | 85.3916 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1636
2024-12-18 | 19:48 | 21.9577 | 85.3917 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1637
2024-12-18 | 19:48 | 21.9577 | 85.3918 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 10.313 | 1638
2024-12-18 | 19:48 | 21.9576 | 85.3919 | 0 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1639
2024-12-18 | 19:48 | 21.9575 | 85.3919 | 0 | 10.12 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1640
2024-12-18 | 19:48 | 21.9574 | 85.3919 | 0 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1641
2024-12-18 | 19:48 | 21.9573 | 85.3919 | 5.24 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1642
2024-12-18 | 19:48 | 21.9572 | 85.3919 | 3.16 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1643
2024-12-18 | 19:48 | 21.957 | 85.3918 | 21.12 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 24.5139 | 1644
2024-12-18 | 19:48 | 21.9569 | 85.3918 | 12.8 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 11.12 | 1645
2024-12-18 | 19:48 | 21.9568 | 85.3918 | 10.12 | 5.24 | 6 | HAUL ROAD (PIT-1 16D) | 11.12 | 1646
2024-12-18 | 19:48 | 21.9567 | 85.3917 | 7.58 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 15.1662 | 1647
2024-12-18 | 19:48 | 21.9566 | 85.3917 | 5.24 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1648
2024-12-18 | 19:48 | 21.9565 | 85.3917 | 1.39 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1649
2024-12-18 | 19:48 | 21.9564 | 85.3916 | 1.39 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1650
2024-12-18 | 19:48 | 21.9563 | 85.3916 | 3.16 | 10.12 | 6 | HAUL ROAD (PIT-1 16D) | 11.12 | 1651
2024-12-18 | 19:48 | 21.9562 | 85.3915 | 15.57 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1652
2024-12-18 | 19:48 | 21.9561 | 85.3915 | 21.12 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1653
2024-12-18 | 19:48 | 21.956 | 85.3914 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1654
2024-12-18 | 19:48 | 21.9558 | 85.3913 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 24.5139 | 1655
2024-12-18 | 19:48 | 21.9557 | 85.3913 | 0 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1656
2024-12-18 | 19:48 | 21.9556 | 85.3913 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1657
2024-12-18 | 19:48 | 21.9555 | 85.3912 | 0 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1658
2024-12-18 | 19:49 | 21.9554 | 85.3911 | 0 | 1.39 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1659
2024-12-18 | 19:49 | 21.9553 | 85.3911 | 0 | 3.16 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1660
2024-12-18 | 19:49 | 21.9552 | 85.391 | 0 | 10.12 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1661
2024-12-18 | 19:49 | 21.955 | 85.391 | 0 | 12.8 | 6 | HAUL ROAD (PIT-1 16D) | 22.2392 | 1662
2024-12-18 | 19:49 | 21.9549 | 85.3909 | 0 | 15.57 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1663
2024-12-18 | 19:49 | 21.9548 | 85.3909 | 7.58 | 21.12 | 6 | HAUL ROAD (PIT-1 16D) | 11.1196 | 1664
2024-12-18 | 19:49 | 21.9547 | 85.3908 | 128.79 | 21.12 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1665
2024-12-18 | 19:49 | 21.9546 | 85.3907 | 18.36 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1666
2024-12-18 | 19:49 | 21.9545 | 85.3907 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.12 | 1667
2024-12-18 | 19:49 | 21.9543 | 85.3906 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 24.5141 | 1668
2024-12-18 | 19:49 | 21.9542 | 85.3906 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.12 | 1669
2024-12-18 | 19:49 | 21.9541 | 85.3905 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1670
2024-12-18 | 19:49 | 21.954 | 85.3905 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1671
2024-12-18 | 19:49 | 21.9539 | 85.3904 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 15.1659 | 1672
2024-12-18 | 19:49 | 21.9538 | 85.3904 | 0 | 0 | 6 | HAUL ROAD (PIT-1 16D) | 11.1192 | 1673
2024-12-18 | 19:49 | 21.9536 | 85.3903 | 0 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 24.5141 | 1674
2024-12-18 | 19:49 | 21.9535 | 85.3903 | 10.12 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1675
2024-12-18 | 19:49 | 21.9534 | 85.3902 | 15.57 | 5.24 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1659 | 1676
2024-12-18 | 19:49 | 21.9533 | 85.3902 | 12.8 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1677
2024-12-18 | 19:49 | 21.9531 | 85.3901 | 7.58 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 24.5143 | 1678
2024-12-18 | 19:49 | 21.953 | 85.3901 | 10.12 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1679
2024-12-18 | 19:49 | 21.9529 | 85.39 | 7.58 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1659 | 1680
2024-12-18 | 19:49 | 21.9528 | 85.39 | 5.24 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1681
2024-12-18 | 19:49 | 21.9527 | 85.39 | 1.39 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1682
2024-12-18 | 19:49 | 21.9525 | 85.3899 | 1.39 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 24.5139 | 1683
2024-12-18 | 19:49 | 21.9524 | 85.3899 | 0 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1684
2024-12-18 | 19:49 | 21.9523 | 85.3898 | 1.39 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1659 | 1685
2024-12-18 | 19:49 | 21.9522 | 85.3898 | 3.16 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1686
2024-12-18 | 19:49 | 21.9521 | 85.3898 | 1.39 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1687
2024-12-18 | 19:49 | 21.952 | 85.3898 | 0 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1688
2024-12-18 | 19:50 | 21.9518 | 85.3898 | 0 | 18.36 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 22.2388 | 1689
2024-12-18 | 19:50 | 21.9517 | 85.3898 | 21.12 | 7.58 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1690
2024-12-18 | 19:50 | 21.9516 | 85.3897 | 10.12 | 36.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1665 | 1691
2024-12-18 | 19:50 | 21.9515 | 85.3897 | 47.04 | 5.24 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1692
2024-12-18 | 19:50 | 21.9514 | 85.3897 | 7.58 | 21.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1693
2024-12-18 | 19:50 | 21.9514 | 85.3897 | 15.57 | 7.58 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0 | 1694
2024-12-18 | 19:50 | 21.9513 | 85.3897 | 1.39 | 23.79 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1695
2024-12-18 | 19:50 | 21.9512 | 85.3896 | 12.8 | 12.8 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1659 | 1696
2024-12-18 | 19:50 | 21.9511 | 85.3896 | 3.16 | 30.73 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1697
2024-12-18 | 19:50 | 21.951 | 85.3896 | 15.57 | 21.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1698
2024-12-18 | 19:50 | 21.9509 | 85.3895 | 12.8 | 21.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1662 | 1699
2024-12-18 | 19:50 | 21.9508 | 85.3895 | 5.24 | 10.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1700
2024-12-18 | 19:50 | 21.9507 | 85.3895 | 0 | 10.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1701
2024-12-18 | 19:50 | 21.9507 | 85.3894 | 5.24 | 15.57 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1702
2024-12-18 | 19:50 | 21.9506 | 85.3894 | 10.12 | 21.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1703
2024-12-18 | 19:50 | 21.9505 | 85.3893 | 7.58 | 15.57 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1659 | 1704
2024-12-18 | 19:50 | 21.9504 | 85.3892 | 3.16 | 18.36 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1659 | 1705
2024-12-18 | 19:50 | 21.9503 | 85.3891 | 12.8 | 18.36 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1662 | 1706
2024-12-18 | 19:50 | 21.9503 | 85.389 | 23.79 | 7.58 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3135 | 1707
2024-12-18 | 19:50 | 21.9502 | 85.3889 | 21.12 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1662 | 1708
2024-12-18 | 19:50 | 21.9502 | 85.3888 | 3.16 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1709
2024-12-18 | 19:50 | 21.9501 | 85.3887 | 0 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1662 | 1710
2024-12-18 | 19:50 | 21.9501 | 85.3886 | 0 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1711
2024-12-18 | 19:50 | 21.9501 | 85.3885 | 0 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1712
2024-12-18 | 19:50 | 21.9501 | 85.3883 | 0 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 20.6272 | 1713
2024-12-18 | 19:50 | 21.9501 | 85.3882 | 0 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1714
2024-12-18 | 19:50 | 21.9501 | 85.3882 | 0 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0.094935 | 1715
2024-12-18 | 19:50 | 21.95 | 85.3881 | 0 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1662 | 1716
2024-12-18 | 19:50 | 21.95 | 85.3881 | 1.39 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0.094935 | 1717
2024-12-18 | 19:50 | 21.95 | 85.388 | 12.8 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1718
2024-12-18 | 19:51 | 21.95 | 85.388 | 12.8 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0.094935 | 1719
2024-12-18 | 19:51 | 21.95 | 85.388 | 12.8 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0.094935 | 1720
2024-12-18 | 19:51 | 21.95 | 85.388 | 12.8 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0.094935 | 1721
2024-12-18 | 19:51 | 21.95 | 85.388 | 12.8 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0.094935 | 1722
2024-12-18 | 19:51 | 21.95 | 85.388 | 12.8 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0.094935 | 1723
2024-12-18 | 19:51 | 21.95 | 85.388 | 12.8 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0.094935 | 1724
2024-12-18 | 19:51 | 21.9501 | 85.388 | 12.8 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1725
2024-12-18 | 19:51 | 21.9501 | 85.388 | 12.8 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0.094935 | 1726
2024-12-18 | 19:51 | 21.9501 | 85.388 | 1.39 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0.094935 | 1727
2024-12-18 | 19:51 | 21.9502 | 85.3881 | 0 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1662 | 1728
2024-12-18 | 19:51 | 21.9502 | 85.3881 | 0 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0.094935 | 1729
2024-12-18 | 19:51 | 21.9503 | 85.3882 | 0 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1662 | 1730
2024-12-18 | 19:51 | 21.9503 | 85.3882 | 0 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0 | 1731
2024-12-18 | 19:51 | 21.9504 | 85.3883 | 7.58 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1662 | 1732
2024-12-18 | 19:51 | 21.9504 | 85.3883 | 12.8 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0 | 1733
2024-12-18 | 19:51 | 21.9505 | 85.3884 | 3.16 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1659 | 1734
2024-12-18 | 19:51 | 21.9505 | 85.3884 | 7.58 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0 | 1735
2024-12-18 | 19:51 | 21.9506 | 85.3885 | 5.24 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1659 | 1736
2024-12-18 | 19:51 | 21.9506 | 85.3886 | 3.16 | 5.24 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3135 | 1737
2024-12-18 | 19:51 | 21.9507 | 85.3886 | 5.24 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1738
2024-12-18 | 19:51 | 21.9507 | 85.3887 | 7.58 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1739
2024-12-18 | 19:51 | 21.9508 | 85.3887 | 7.58 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1740
2024-12-18 | 19:51 | 21.9508 | 85.3888 | 7.58 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.313 | 1741
2024-12-18 | 19:51 | 21.9509 | 85.3889 | 5.24 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1659 | 1742
2024-12-18 | 19:51 | 21.9509 | 85.3889 | 1.39 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0.094935 | 1743
2024-12-18 | 19:51 | 21.951 | 85.3889 | 0 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1744
2024-12-18 | 19:51 | 21.951 | 85.3888 | 0 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3135 | 1745
2024-12-18 | 19:51 | 21.951 | 85.3888 | 5.24 | 5.24 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0 | 1746
2024-12-18 | 19:51 | 21.951 | 85.3888 | 15.57 | 21.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0 | 1747
2024-12-18 | 19:51 | 21.951 | 85.3888 | 21.12 | 21.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0 | 1748
2024-12-18 | 19:52 | 21.951 | 85.3888 | 18.36 | 21.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0 | 1749
2024-12-18 | 19:52 | 21.951 | 85.3888 | 12.8 | 21.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0 | 1750
2024-12-18 | 19:52 | 21.9511 | 85.3888 | 5.24 | 15.57 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1751
2024-12-18 | 19:52 | 21.9511 | 85.3888 | 3.16 | 10.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0 | 1752
2024-12-18 | 19:52 | 21.951 | 85.3888 | 3.16 | 12.8 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1753
2024-12-18 | 19:52 | 21.951 | 85.3889 | 5.24 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3135 | 1754
2024-12-18 | 19:52 | 21.9509 | 85.3889 | 1.39 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1755
2024-12-18 | 19:52 | 21.9508 | 85.3888 | 3.16 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1659 | 1756
2024-12-18 | 19:52 | 21.9507 | 85.3887 | 7.58 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1662 | 1757
2024-12-18 | 19:52 | 21.9507 | 85.3887 | 7.58 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0.094935 | 1758
2024-12-18 | 19:52 | 21.9506 | 85.3886 | 3.16 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1659 | 1759
2024-12-18 | 19:52 | 21.9505 | 85.3885 | 1.39 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1659 | 1760
2024-12-18 | 19:52 | 21.9505 | 85.3885 | 15.57 | 15.57 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0 | 1761
2024-12-18 | 19:52 | 21.9504 | 85.3884 | 44.32 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1659 | 1762
2024-12-18 | 19:52 | 21.9504 | 85.3883 | 10.12 | 12.8 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3135 | 1763
2024-12-18 | 19:52 | 21.9503 | 85.3883 | 60.64 | 10.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1764
2024-12-18 | 19:52 | 21.9503 | 85.3882 | 41.6 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3135 | 1765
2024-12-18 | 19:52 | 21.9502 | 85.3882 | 0 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1766
2024-12-18 | 19:52 | 21.9502 | 85.3881 | 0 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1767
2024-12-18 | 19:52 | 21.9501 | 85.3881 | 0 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1768
2024-12-18 | 19:52 | 21.9501 | 85.388 | 0 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1769
2024-12-18 | 19:52 | 21.95 | 85.388 | 3.16 | 7.58 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1770
2024-12-18 | 19:52 | 21.9499 | 85.3879 | 44.32 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1662 | 1771
2024-12-18 | 19:52 | 21.9499 | 85.3878 | 7.58 | 7.58 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3135 | 1772
2024-12-18 | 19:52 | 21.9498 | 85.3878 | 63.36 | 10.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.12 | 1773
2024-12-18 | 19:52 | 21.9497 | 85.3877 | 18.36 | 21.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1662 | 1774
2024-12-18 | 19:52 | 21.9496 | 85.3877 | 136.99 | 7.58 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1775
2024-12-18 | 19:52 | 21.9495 | 85.3876 | 71.53 | 26.31 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1659 | 1776
2024-12-18 | 19:52 | 21.9494 | 85.3876 | 18.36 | 23.79 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1777
2024-12-18 | 19:52 | 21.9492 | 85.3875 | 52.48 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 24.5141 | 1778
2024-12-18 | 19:53 | 21.9491 | 85.3875 | 96.05 | 21.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1779
2024-12-18 | 19:53 | 21.949 | 85.3875 | 26.31 | 30.73 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1780
2024-12-18 | 19:53 | 21.9489 | 85.3875 | 41.6 | 18.36 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1781
2024-12-18 | 19:53 | 21.9487 | 85.3875 | 66.08 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 22.2392 | 1782
2024-12-18 | 19:53 | 21.9486 | 85.3874 | 30.73 | 26.31 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1665 | 1783
2024-12-18 | 19:53 | 21.9485 | 85.3874 | 30.73 | 0 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1784
2024-12-18 | 19:53 | 21.9484 | 85.3874 | 0 | 7.58 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1785
2024-12-18 | 19:53 | 21.9483 | 85.3874 | 15.57 | 26.31 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1786
2024-12-18 | 19:53 | 21.9482 | 85.3873 | 23.79 | 7.58 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1659 | 1787
2024-12-18 | 19:53 | 21.9481 | 85.3873 | 7.58 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1788
2024-12-18 | 19:53 | 21.948 | 85.3873 | 3.16 | 10.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1789
2024-12-18 | 19:53 | 21.9479 | 85.3873 | 18.36 | 5.24 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1790
2024-12-18 | 19:53 | 21.9478 | 85.3872 | 3.16 | 10.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1662 | 1791
2024-12-18 | 19:53 | 21.9477 | 85.3872 | 12.8 | 10.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.12 | 1792
2024-12-18 | 19:53 | 21.9476 | 85.3872 | 18.36 | 15.57 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1793
2024-12-18 | 19:53 | 21.9475 | 85.3871 | 10.12 | 15.57 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1665 | 1794
2024-12-18 | 19:53 | 21.9474 | 85.3871 | 38.88 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1795
2024-12-18 | 19:53 | 21.9473 | 85.3871 | 1.39 | 12.8 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.12 | 1796
2024-12-18 | 19:53 | 21.9472 | 85.387 | 15.57 | 10.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1665 | 1797
2024-12-18 | 19:53 | 21.9471 | 85.387 | 10.12 | 12.8 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1798
2024-12-18 | 19:53 | 21.9471 | 85.387 | 18.36 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 0 | 1799
2024-12-18 | 19:53 | 21.947 | 85.387 | 0 | 10.12 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1800
2024-12-18 | 19:53 | 21.9469 | 85.3869 | 10.12 | 18.36 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1665 | 1801
2024-12-18 | 19:53 | 21.9469 | 85.3868 | 18.36 | 3.16 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1802
2024-12-18 | 19:53 | 21.9469 | 85.3867 | 26.31 | 26.31 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1803
2024-12-18 | 19:53 | 21.9469 | 85.3866 | 60.64 | 47.04 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1804
2024-12-18 | 19:53 | 21.9469 | 85.3865 | 93.32 | 7.58 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1805
2024-12-18 | 19:53 | 21.9469 | 85.3864 | 41.6 | 23.79 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1806
2024-12-18 | 19:53 | 21.947 | 85.3864 | 55.2 | 23.79 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1192 | 1807
2024-12-18 | 19:53 | 21.947 | 85.3863 | 33.45 | 26.31 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3144 | 1808
2024-12-18 | 19:54 | 21.947 | 85.3862 | 82.42 | 15.57 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3144 | 1809
2024-12-18 | 19:54 | 21.9471 | 85.3861 | 60.64 | 41.6 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1665 | 1810
2024-12-18 | 19:54 | 21.9471 | 85.386 | 93.32 | 26.31 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1811
2024-12-18 | 19:54 | 21.9472 | 85.3859 | 71.53 | 33.45 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1665 | 1812
2024-12-18 | 19:54 | 21.9472 | 85.3858 | 71.53 | 26.31 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1813
2024-12-18 | 19:54 | 21.9472 | 85.3857 | 90.59 | 12.8 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1814
2024-12-18 | 19:54 | 21.9472 | 85.3856 | 49.76 | 26.31 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1815
2024-12-18 | 19:54 | 21.9472 | 85.3855 | 76.97 | 26.31 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1816
2024-12-18 | 19:54 | 21.9472 | 85.3854 | 90.59 | 33.45 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 10.3139 | 1817
2024-12-18 | 19:54 | 21.9471 | 85.3853 | 98.77 | 1.39 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1665 | 1818
2024-12-18 | 19:54 | 21.9469 | 85.3852 | 60.64 | 33.45 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 24.5143 | 1819
2024-12-18 | 19:54 | 21.9468 | 85.3852 | 71.53 | 33.45 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1820
2024-12-18 | 19:54 | 21.9467 | 85.3851 | 90.59 | 23.79 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1665 | 1821
2024-12-18 | 19:54 | 21.9466 | 85.3851 | 90.59 | 23.79 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 11.1196 | 1822
2024-12-18 | 19:54 | 21.9465 | 85.385 | 60.64 | 47.04 | 6 | HAUL ROAD (TLS TO PIT-11 VIEW) | 15.1665 | 1823
2024-12-18 | 19:54 | 21.9464 | 85.385 | 76.97 | 10.12 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1824
2024-12-18 | 19:54 | 21.9462 | 85.385 | 96.05 | 12.8 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 22.239 | 1825
2024-12-18 | 19:54 | 21.9461 | 85.3849 | 33.45 | 12.8 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 15.1665 | 1826
2024-12-18 | 19:54 | 21.946 | 85.3849 | 23.79 | 12.8 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1827
2024-12-18 | 19:54 | 21.9459 | 85.3849 | 36.16 | 21.12 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1828
2024-12-18 | 19:54 | 21.9457 | 85.3848 | 23.79 | 23.79 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 24.5143 | 1829
2024-12-18 | 19:54 | 21.9456 | 85.3848 | 36.16 | 12.8 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1830
2024-12-18 | 19:54 | 21.9455 | 85.3848 | 26.31 | 10.12 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1831
2024-12-18 | 19:54 | 21.9453 | 85.3848 | 30.73 | 23.79 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 22.2388 | 1832
2024-12-18 | 19:54 | 21.9452 | 85.3848 | 41.6 | 36.16 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1833
2024-12-18 | 19:54 | 21.9451 | 85.3848 | 60.64 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1834
2024-12-18 | 19:54 | 21.9449 | 85.3848 | 71.53 | 21.12 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 22.239 | 1835
2024-12-18 | 19:54 | 21.9448 | 85.3848 | 36.16 | 12.8 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1836
2024-12-18 | 19:54 | 21.9447 | 85.3848 | 21.12 | 15.57 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1837
2024-12-18 | 19:54 | 21.9446 | 85.3848 | 5.24 | 5.24 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1838
2024-12-18 | 19:55 | 21.9445 | 85.3848 | 7.58 | 7.58 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1839
2024-12-18 | 19:55 | 21.9444 | 85.3847 | 15.57 | 15.57 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 15.1662 | 1840
2024-12-18 | 19:55 | 21.9443 | 85.3847 | 23.79 | 23.79 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1841
2024-12-18 | 19:55 | 21.9443 | 85.3847 | 36.16 | 41.6 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0.094935 | 1842
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 74.25 | 33.45 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.12 | 1843
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 66.08 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1844
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 63.36 | 30.73 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1845
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 68.8 | 30.73 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1846
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 68.8 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1847
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 68.8 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1848
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 68.8 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1849
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 68.8 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1850
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1851
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 68.8 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1852
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1853
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1854
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 63.36 | 38.88 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1855
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 63.36 | 30.73 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1856
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 68.8 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1857
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1858
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 68.8 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1859
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1860
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 68.8 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1861
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1862
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1863
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 63.36 | 36.16 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1864
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 63.36 | 44.32 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1865
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 63.36 | 44.32 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1866
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 63.36 | 44.32 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1867
2024-12-18 | 19:55 | 21.9442 | 85.3847 | 63.36 | 44.32 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1868
2024-12-18 | 19:56 | 21.9442 | 85.3847 | 63.36 | 36.16 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1869
2024-12-18 | 19:56 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1870
2024-12-18 | 19:56 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1871
2024-12-18 | 19:56 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1872
2024-12-18 | 19:56 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1873
2024-12-18 | 19:56 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1874
2024-12-18 | 19:56 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1875
2024-12-18 | 19:56 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1876
2024-12-18 | 19:56 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1877
2024-12-18 | 19:56 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1878
2024-12-18 | 19:56 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1879
2024-12-18 | 19:56 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1880
2024-12-18 | 19:56 | 21.9442 | 85.3847 | 63.36 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1881
2024-12-18 | 19:56 | 21.9442 | 85.3847 | 63.36 | 36.16 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1882
2024-12-18 | 19:56 | 21.9441 | 85.3847 | 68.8 | 55.2 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1883
2024-12-18 | 19:56 | 21.9441 | 85.3847 | 79.7 | 57.92 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1884
2024-12-18 | 19:56 | 21.944 | 85.3846 | 87.87 | 36.16 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 15.1665 | 1885
2024-12-18 | 19:56 | 21.944 | 85.3846 | 71.53 | 23.79 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1886
2024-12-18 | 19:56 | 21.9439 | 85.3846 | 66.08 | 15.57 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1887
2024-12-18 | 19:56 | 21.9438 | 85.3846 | 60.64 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1888
2024-12-18 | 19:56 | 21.9438 | 85.3846 | 60.64 | 3.16 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0.094935 | 1889
2024-12-18 | 19:56 | 21.9437 | 85.3846 | 38.88 | 3.16 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1890
2024-12-18 | 19:56 | 21.9436 | 85.3846 | 23.79 | 3.16 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1891
2024-12-18 | 19:56 | 21.9435 | 85.3846 | 15.57 | 3.16 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1892
2024-12-18 | 19:56 | 21.9434 | 85.3845 | 10.12 | 10.12 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 15.1662 | 1893
2024-12-18 | 19:56 | 21.9433 | 85.3845 | 12.8 | 7.58 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1894
2024-12-18 | 19:56 | 21.9433 | 85.3845 | 18.36 | 21.12 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1895
2024-12-18 | 19:56 | 21.9432 | 85.3845 | 30.73 | 10.12 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1896
2024-12-18 | 19:56 | 21.9431 | 85.3845 | 33.45 | 21.12 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1897
2024-12-18 | 19:56 | 21.943 | 85.3844 | 52.48 | 1.39 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 15.1668 | 1898
2024-12-18 | 19:57 | 21.9429 | 85.3844 | 18.36 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1899
2024-12-18 | 19:57 | 21.9428 | 85.3844 | 0 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.12 | 1900
2024-12-18 | 19:57 | 21.9428 | 85.3843 | 0 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 10.3144 | 1901
2024-12-18 | 19:57 | 21.9427 | 85.3843 | 0 | 1.39 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.12 | 1902
2024-12-18 | 19:57 | 21.9426 | 85.3843 | 0 | 1.39 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.12 | 1903
2024-12-18 | 19:57 | 21.9425 | 85.3843 | 15.57 | 5.24 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1904
2024-12-18 | 19:57 | 21.9424 | 85.3844 | 10.12 | 3.16 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 15.1665 | 1905
2024-12-18 | 19:57 | 21.9423 | 85.3844 | 3.16 | 3.16 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1906
2024-12-18 | 19:57 | 21.9422 | 85.3844 | 1.39 | 1.39 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1907
2024-12-18 | 19:57 | 21.9422 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 10.3139 | 1908
2024-12-18 | 19:57 | 21.9421 | 85.3845 | 0 | 1.39 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1909
2024-12-18 | 19:57 | 21.942 | 85.3845 | 0 | 1.39 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.12 | 1910
2024-12-18 | 19:57 | 21.9419 | 85.3846 | 0 | 1.39 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 15.1665 | 1911
2024-12-18 | 19:57 | 21.9418 | 85.3846 | 0 | 3.16 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1912
2024-12-18 | 19:57 | 21.9418 | 85.3847 | 5.24 | 7.58 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 10.3139 | 1913
2024-12-18 | 19:57 | 21.9417 | 85.3846 | 5.24 | 5.24 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 15.1665 | 1914
2024-12-18 | 19:57 | 21.9417 | 85.3846 | 0 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0.094935 | 1915
2024-12-18 | 19:57 | 21.9417 | 85.3846 | 0 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0.094935 | 1916
2024-12-18 | 19:57 | 21.9417 | 85.3846 | 0 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0.094935 | 1917
2024-12-18 | 19:57 | 21.9418 | 85.3847 | 0 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 15.1665 | 1918
2024-12-18 | 19:57 | 21.9418 | 85.3846 | 0 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 10.3139 | 1919
2024-12-18 | 19:57 | 21.9418 | 85.3846 | 0 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1920
2024-12-18 | 19:57 | 21.9419 | 85.3846 | 0 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1921
2024-12-18 | 19:57 | 21.9419 | 85.3845 | 0 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 10.3144 | 1922
2024-12-18 | 19:57 | 21.942 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1923
2024-12-18 | 19:57 | 21.9421 | 85.3845 | 0 | 5.24 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.12 | 1924
2024-12-18 | 19:57 | 21.9422 | 85.3845 | 0 | 10.12 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1925
2024-12-18 | 19:57 | 21.9423 | 85.3844 | 0 | 3.16 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 15.1662 | 1926
2024-12-18 | 19:57 | 21.9424 | 85.3844 | 0 | 1.39 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1927
2024-12-18 | 19:57 | 21.9425 | 85.3843 | 1.39 | 1.39 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 15.1665 | 1928
2024-12-18 | 19:58 | 21.9426 | 85.3843 | 5.24 | 5.24 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1929
2024-12-18 | 19:58 | 21.9427 | 85.3843 | 5.24 | 1.39 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.12 | 1930
2024-12-18 | 19:58 | 21.9428 | 85.3843 | 0 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.12 | 1931
2024-12-18 | 19:58 | 21.9429 | 85.3843 | 0 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.12 | 1932
2024-12-18 | 19:58 | 21.943 | 85.3843 | 0 | 1.39 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1196 | 1933
2024-12-18 | 19:58 | 21.9431 | 85.3843 | 7.58 | 23.79 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.12 | 1934
2024-12-18 | 19:58 | 21.9432 | 85.3843 | 63.36 | 12.8 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1935
2024-12-18 | 19:58 | 21.9433 | 85.3843 | 41.6 | 26.31 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1936
2024-12-18 | 19:58 | 21.9434 | 85.3843 | 26.31 | 30.73 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1937
2024-12-18 | 19:58 | 21.9435 | 85.3843 | 26.31 | 21.12 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1938
2024-12-18 | 19:58 | 21.9436 | 85.3843 | 23.79 | 30.73 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 11.1192 | 1939
2024-12-18 | 19:58 | 21.9436 | 85.3842 | 23.79 | 15.57 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 10.3139 | 1940
2024-12-18 | 19:58 | 21.9436 | 85.3842 | 15.57 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 0 | 1941
2024-12-18 | 19:58 | 21.9436 | 85.3841 | 5.24 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 10.3139 | 1942
2024-12-18 | 19:58 | 21.9436 | 85.384 | 3.16 | 0 | 6 | HAUL ROAD ( TWIN CANTEEN TO PCH) | 10.3139 | 1943
2024-12-18 | 19:58 | 21.9435 | 85.3839 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1665 | 1944
2024-12-18 | 19:58 | 21.9435 | 85.3838 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 1945
2024-12-18 | 19:58 | 21.9434 | 85.3837 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1662 | 1946
2024-12-18 | 19:58 | 21.9434 | 85.3835 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 20.6278 | 1947
2024-12-18 | 19:58 | 21.9434 | 85.3834 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3135 | 1948
2024-12-18 | 19:58 | 21.9434 | 85.3833 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3135 | 1949
2024-12-18 | 19:58 | 21.9433 | 85.3832 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1662 | 1950
2024-12-18 | 19:58 | 21.9433 | 85.3831 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 1951
2024-12-18 | 19:58 | 21.9432 | 85.3829 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 23.4338 | 1952
2024-12-18 | 19:58 | 21.9432 | 85.3828 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 1953
2024-12-18 | 19:58 | 21.9431 | 85.3828 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 11.1192 | 1954
2024-12-18 | 19:58 | 21.943 | 85.3827 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1668 | 1955
2024-12-18 | 19:58 | 21.9429 | 85.3826 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1665 | 1956
2024-12-18 | 19:58 | 21.9427 | 85.3826 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 22.239 | 1957
2024-12-18 | 19:58 | 21.9426 | 85.3825 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1668 | 1958
2024-12-18 | 19:59 | 21.9425 | 85.3825 | 0 | 1.39 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 11.1192 | 1959
2024-12-18 | 19:59 | 21.9424 | 85.3824 | 7.58 | 10.12 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1665 | 1960
2024-12-18 | 19:59 | 21.9423 | 85.3824 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 11.1192 | 1961
2024-12-18 | 19:59 | 21.9422 | 85.3824 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 11.1192 | 1962
2024-12-18 | 19:59 | 21.942 | 85.3824 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 22.2388 | 1963
2024-12-18 | 19:59 | 21.9419 | 85.3824 | 0 | 1.39 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 11.1196 | 1964
2024-12-18 | 19:59 | 21.9418 | 85.3824 | 26.31 | 7.58 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 11.1196 | 1965
2024-12-18 | 19:59 | 21.9417 | 85.3824 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 11.1196 | 1966
2024-12-18 | 19:59 | 21.9417 | 85.3825 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 1967
2024-12-18 | 19:59 | 21.9416 | 85.3825 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 11.1196 | 1968
2024-12-18 | 19:59 | 21.9415 | 85.3825 | 0 | 5.24 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 11.1192 | 1969
2024-12-18 | 19:59 | 21.9415 | 85.3824 | 1.39 | 7.58 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 1970
2024-12-18 | 19:59 | 21.9415 | 85.3823 | 15.57 | 23.79 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 1971
2024-12-18 | 19:59 | 21.9416 | 85.3822 | 36.16 | 7.58 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1665 | 1972
2024-12-18 | 19:59 | 21.9416 | 85.3821 | 7.58 | 18.36 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 1973
2024-12-18 | 19:59 | 21.9417 | 85.382 | 71.53 | 7.58 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1668 | 1974
2024-12-18 | 19:59 | 21.9417 | 85.382 | 18.36 | 10.12 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 0.094935 | 1975
2024-12-18 | 19:59 | 21.9418 | 85.3819 | 49.76 | 30.73 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1665 | 1976
2024-12-18 | 19:59 | 21.9419 | 85.3818 | 38.88 | 21.12 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1665 | 1977
2024-12-18 | 19:59 | 21.9419 | 85.3817 | 41.6 | 44.32 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 1978
2024-12-18 | 19:59 | 21.942 | 85.3817 | 68.8 | 30.73 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 11.1196 | 1979
2024-12-18 | 19:59 | 21.942 | 85.3816 | 60.64 | 49.76 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 1980
2024-12-18 | 19:59 | 21.942 | 85.3815 | 150.65 | 5.24 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 1981
2024-12-18 | 19:59 | 21.942 | 85.3814 | 44.32 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 1982
2024-12-18 | 19:59 | 21.9419 | 85.3813 | 15.57 | 3.16 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1665 | 1983
2024-12-18 | 19:59 | 21.9419 | 85.3812 | 112.41 | 12.8 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 1984
2024-12-18 | 19:59 | 21.9418 | 85.3811 | 38.88 | 7.58 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1665 | 1985
2024-12-18 | 19:59 | 21.9418 | 85.381 | 47.04 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 1986
2024-12-18 | 19:59 | 21.9418 | 85.3809 | 15.57 | 10.12 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 1987
2024-12-18 | 19:59 | 21.9417 | 85.3808 | 12.8 | 3.16 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1665 | 1988
2024-12-18 | 20:00 | 21.9417 | 85.3807 | 38.88 | 10.12 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 1989
2024-12-18 | 20:00 | 21.9416 | 85.3806 | 18.36 | 3.16 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1668 | 1990
2024-12-18 | 20:00 | 21.9416 | 85.3805 | 63.36 | 3.16 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 1991
2024-12-18 | 20:00 | 21.9415 | 85.3804 | 10.12 | 5.24 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1665 | 1992
2024-12-18 | 20:00 | 21.9415 | 85.3803 | 60.64 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 1993
2024-12-18 | 20:00 | 21.9415 | 85.3802 | 5.24 | 3.16 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 1994
2024-12-18 | 20:00 | 21.9414 | 85.3801 | 26.31 | 3.16 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1665 | 1995
2024-12-18 | 20:00 | 21.9414 | 85.3801 | 26.31 | 10.12 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 0 | 1996
2024-12-18 | 20:00 | 21.9413 | 85.38 | 38.88 | 26.31 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1668 | 1997
2024-12-18 | 20:00 | 21.9413 | 85.3799 | 101.5 | 10.12 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 1998
2024-12-18 | 20:00 | 21.9412 | 85.3798 | 26.31 | 1.39 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1665 | 1999
2024-12-18 | 20:00 | 21.9412 | 85.3797 | 36.16 | 3.16 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 2000
2024-12-18 | 20:00 | 21.9411 | 85.3796 | 23.79 | 26.31 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1668 | 2001
2024-12-18 | 20:00 | 21.9411 | 85.3795 | 109.68 | 10.12 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 2002
2024-12-18 | 20:00 | 21.941 | 85.3795 | 74.25 | 26.31 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 11.1192 | 2003
2024-12-18 | 20:00 | 21.941 | 85.3794 | 90.59 | 1.39 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 2004
2024-12-18 | 20:00 | 21.9409 | 85.3793 | 3.16 | 1.39 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1668 | 2005
2024-12-18 | 20:00 | 21.9409 | 85.3793 | 1.39 | 5.24 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 0 | 2006
2024-12-18 | 20:00 | 21.9408 | 85.3793 | 1.39 | 1.39 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 11.1192 | 2007
2024-12-18 | 20:00 | 21.9408 | 85.3792 | 0 | 7.58 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 2008
2024-12-18 | 20:00 | 21.9408 | 85.3792 | 1.39 | 7.58 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 0 | 2009
2024-12-18 | 20:00 | 21.9407 | 85.3791 | 10.12 | 7.58 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1665 | 2010
2024-12-18 | 20:00 | 21.9407 | 85.379 | 12.8 | 10.12 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 2011
2024-12-18 | 20:00 | 21.9406 | 85.379 | 7.58 | 18.36 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 11.1192 | 2012
2024-12-18 | 20:00 | 21.9406 | 85.379 | 18.36 | 18.36 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 0 | 2013
2024-12-18 | 20:00 | 21.9406 | 85.3789 | 30.73 | 3.16 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 2014
2024-12-18 | 20:00 | 21.9406 | 85.3789 | 26.31 | 1.39 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 0 | 2015
2024-12-18 | 20:00 | 21.9406 | 85.3788 | 7.58 | 3.16 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 2016
2024-12-18 | 20:00 | 21.9405 | 85.3788 | 3.16 | 3.16 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 11.1196 | 2017
2024-12-18 | 20:00 | 21.9405 | 85.3788 | 0 | 5.24 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 0.094935 | 2018
2024-12-18 | 20:01 | 21.9405 | 85.3787 | 0 | 7.58 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3148 | 2019
2024-12-18 | 20:01 | 21.9404 | 85.3786 | 0 | 12.8 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1668 | 2020
2024-12-18 | 20:01 | 21.9404 | 85.3786 | 0 | 21.12 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 0 | 2021
2024-12-18 | 20:01 | 21.9404 | 85.3785 | 0 | 30.73 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 2022
2024-12-18 | 20:01 | 21.9403 | 85.3785 | 3.16 | 18.36 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 11.1196 | 2023
2024-12-18 | 20:01 | 21.9403 | 85.3784 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3144 | 2024
2024-12-18 | 20:01 | 21.9402 | 85.3783 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 15.1668 | 2025
2024-12-18 | 20:01 | 21.9402 | 85.3783 | 0 | 0 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 0 | 2026
2024-12-18 | 20:01 | 21.9402 | 85.3782 | 0 | 3.16 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 2027
2024-12-18 | 20:01 | 21.9402 | 85.3781 | 3.16 | 7.58 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 2028
2024-12-18 | 20:01 | 21.9402 | 85.3781 | 23.79 | 10.12 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 0 | 2029
2024-12-18 | 20:01 | 21.9402 | 85.378 | 26.31 | 10.12 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 2030
2024-12-18 | 20:01 | 21.9402 | 85.3779 | 21.12 | 18.36 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 2031
2024-12-18 | 20:01 | 21.9402 | 85.3778 | 49.76 | 7.58 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 2032
2024-12-18 | 20:01 | 21.9402 | 85.3777 | 23.79 | 23.79 | 6 | HAUL ROAD (TWIN CANTEEN TO METSO) | 10.3139 | 2033
2024-12-18 | 20:01 | 21.9403 | 85.3777 | 41.6 | 21.12 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1196 | 2034
2024-12-18 | 20:01 | 21.9403 | 85.3777 | 49.76 | 38.88 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2035
2024-12-18 | 20:01 | 21.9404 | 85.3776 | 68.8 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1668 | 2036
2024-12-18 | 20:01 | 21.9405 | 85.3776 | 18.36 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1196 | 2037
2024-12-18 | 20:01 | 21.9405 | 85.3776 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0.094935 | 2038
2024-12-18 | 20:01 | 21.9406 | 85.3776 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1196 | 2039
2024-12-18 | 20:01 | 21.9407 | 85.3777 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1665 | 2040
2024-12-18 | 20:01 | 21.9407 | 85.3777 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2041
2024-12-18 | 20:01 | 21.9408 | 85.3777 | 0 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2042
2024-12-18 | 20:01 | 21.9409 | 85.3777 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2043
2024-12-18 | 20:01 | 21.941 | 85.3778 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1668 | 2044
2024-12-18 | 20:01 | 21.9411 | 85.3778 | 0 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2045
2024-12-18 | 20:01 | 21.9412 | 85.3779 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1668 | 2046
2024-12-18 | 20:01 | 21.9413 | 85.3779 | 0 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2047
2024-12-18 | 20:01 | 21.9413 | 85.378 | 1.39 | 5.24 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3144 | 2048
2024-12-18 | 20:02 | 21.9414 | 85.3781 | 7.58 | 12.8 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1668 | 2049
2024-12-18 | 20:02 | 21.9414 | 85.3782 | 26.31 | 18.36 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3144 | 2050
2024-12-18 | 20:02 | 21.9414 | 85.3782 | 47.04 | 15.57 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2051
2024-12-18 | 20:02 | 21.9414 | 85.3783 | 55.2 | 3.16 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3144 | 2052
2024-12-18 | 20:02 | 21.9415 | 85.3783 | 52.48 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2053
2024-12-18 | 20:02 | 21.9415 | 85.3783 | 41.6 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2054
2024-12-18 | 20:02 | 21.9415 | 85.3783 | 38.88 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2055
2024-12-18 | 20:02 | 21.9415 | 85.3783 | 44.32 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2056
2024-12-18 | 20:02 | 21.9414 | 85.3783 | 47.04 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2057
2024-12-18 | 20:02 | 21.9414 | 85.3783 | 49.76 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2058
2024-12-18 | 20:02 | 21.9414 | 85.3782 | 49.76 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3144 | 2059
2024-12-18 | 20:02 | 21.9414 | 85.3782 | 44.32 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2060
2024-12-18 | 20:02 | 21.9414 | 85.3781 | 30.73 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3144 | 2061
2024-12-18 | 20:02 | 21.9413 | 85.378 | 5.24 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1668 | 2062
2024-12-18 | 20:02 | 21.9412 | 85.3779 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1665 | 2063
2024-12-18 | 20:02 | 21.9411 | 85.3779 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1196 | 2064
2024-12-18 | 20:02 | 21.941 | 85.3778 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1665 | 2065
2024-12-18 | 20:02 | 21.9409 | 85.3777 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1668 | 2066
2024-12-18 | 20:02 | 21.9408 | 85.3777 | 0 | 3.16 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2067
2024-12-18 | 20:02 | 21.9407 | 85.3777 | 0 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2068
2024-12-18 | 20:02 | 21.9406 | 85.3777 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2069
2024-12-18 | 20:02 | 21.9405 | 85.3776 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1668 | 2070
2024-12-18 | 20:02 | 21.9404 | 85.3776 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1196 | 2071
2024-12-18 | 20:02 | 21.9403 | 85.3777 | 10.12 | 23.79 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1668 | 2072
2024-12-18 | 20:02 | 21.9403 | 85.3777 | 74.25 | 3.16 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2073
2024-12-18 | 20:02 | 21.9402 | 85.3778 | 41.6 | 15.57 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1668 | 2074
2024-12-18 | 20:02 | 21.9402 | 85.3779 | 23.79 | 12.8 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3139 | 2075
2024-12-18 | 20:02 | 21.9402 | 85.378 | 60.64 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3139 | 2076
2024-12-18 | 20:02 | 21.9402 | 85.3781 | 21.12 | 10.12 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3139 | 2077
2024-12-18 | 20:02 | 21.9402 | 85.3781 | 55.2 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2078
2024-12-18 | 20:03 | 21.9402 | 85.3782 | 5.24 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3139 | 2079
2024-12-18 | 20:03 | 21.9402 | 85.3783 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3139 | 2080
2024-12-18 | 20:03 | 21.9403 | 85.3784 | 0 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1668 | 2081
2024-12-18 | 20:03 | 21.9403 | 85.3785 | 0 | 3.16 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3144 | 2082
2024-12-18 | 20:03 | 21.9403 | 85.3785 | 0 | 5.24 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2083
2024-12-18 | 20:03 | 21.9404 | 85.3786 | 0 | 3.16 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1668 | 2084
2024-12-18 | 20:03 | 21.9404 | 85.3786 | 0 | 3.16 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2085
2024-12-18 | 20:03 | 21.9405 | 85.3787 | 0 | 7.58 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1668 | 2086
2024-12-18 | 20:03 | 21.9405 | 85.3787 | 0 | 10.12 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0.094935 | 2087
2024-12-18 | 20:03 | 21.9405 | 85.3787 | 0 | 15.57 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0.094935 | 2088
2024-12-18 | 20:03 | 21.9406 | 85.3787 | 0 | 12.8 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1196 | 2089
2024-12-18 | 20:03 | 21.9406 | 85.3787 | 0 | 18.36 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2090
2024-12-18 | 20:03 | 21.9406 | 85.3787 | 0 | 18.36 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2091
2024-12-18 | 20:03 | 21.9406 | 85.3787 | 0 | 18.36 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2092
2024-12-18 | 20:03 | 21.9406 | 85.3787 | 0 | 18.36 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2093
2024-12-18 | 20:03 | 21.9406 | 85.3787 | 0 | 18.36 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2094
2024-12-18 | 20:03 | 21.9407 | 85.3787 | 0 | 21.12 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2095
2024-12-18 | 20:03 | 21.9407 | 85.3786 | 0 | 18.36 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3144 | 2096
2024-12-18 | 20:03 | 21.9407 | 85.3785 | 0 | 7.58 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3144 | 2097
2024-12-18 | 20:03 | 21.9408 | 85.3785 | 3.16 | 5.24 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2098
2024-12-18 | 20:03 | 21.9408 | 85.3784 | 7.58 | 7.58 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3139 | 2099
2024-12-18 | 20:03 | 21.9408 | 85.3784 | 5.24 | 7.58 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2100
2024-12-18 | 20:03 | 21.9409 | 85.3784 | 10.12 | 3.16 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2101
2024-12-18 | 20:03 | 21.9409 | 85.3785 | 21.12 | 23.79 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3144 | 2102
2024-12-18 | 20:03 | 21.9409 | 85.3785 | 26.31 | 33.45 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2103
2024-12-18 | 20:03 | 21.9408 | 85.3785 | 15.57 | 7.58 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2104
2024-12-18 | 20:03 | 21.9408 | 85.3785 | 10.12 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2105
2024-12-18 | 20:03 | 21.9408 | 85.3785 | 1.39 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2106
2024-12-18 | 20:03 | 21.9407 | 85.3785 | 1.39 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2107
2024-12-18 | 20:03 | 21.9407 | 85.3786 | 0 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3144 | 2108
2024-12-18 | 20:04 | 21.9407 | 85.3786 | 0 | 5.24 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2109
2024-12-18 | 20:04 | 21.9406 | 85.3787 | 0 | 3.16 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1665 | 2110
2024-12-18 | 20:04 | 21.9406 | 85.3788 | 0 | 3.16 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3144 | 2111
2024-12-18 | 20:04 | 21.9406 | 85.3788 | 0 | 10.12 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2112
2024-12-18 | 20:04 | 21.9406 | 85.3789 | 3.16 | 26.31 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3144 | 2113
2024-12-18 | 20:04 | 21.9407 | 85.3789 | 18.36 | 5.24 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2114
2024-12-18 | 20:04 | 21.9407 | 85.3789 | 12.8 | 23.79 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2115
2024-12-18 | 20:04 | 21.9408 | 85.3789 | 38.88 | 47.04 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2116
2024-12-18 | 20:04 | 21.9409 | 85.3789 | 60.64 | 18.36 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2117
2024-12-18 | 20:04 | 21.9409 | 85.3789 | 7.58 | 23.79 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2118
2024-12-18 | 20:04 | 21.941 | 85.3789 | 3.16 | 18.36 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1196 | 2119
2024-12-18 | 20:04 | 21.941 | 85.3788 | 10.12 | 10.12 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 10.3139 | 2120
2024-12-18 | 20:04 | 21.9411 | 85.3788 | 7.58 | 12.8 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2121
2024-12-18 | 20:04 | 21.9412 | 85.3789 | 15.57 | 12.8 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1668 | 2122
2024-12-18 | 20:04 | 21.9412 | 85.3789 | 10.12 | 3.16 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2123
2024-12-18 | 20:04 | 21.9413 | 85.3789 | 5.24 | 7.58 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 11.1192 | 2124
2024-12-18 | 20:04 | 21.9413 | 85.3789 | 3.16 | 10.12 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2125
2024-12-18 | 20:04 | 21.9413 | 85.3789 | 1.39 | 3.16 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2126
2024-12-18 | 20:04 | 21.9413 | 85.3789 | 1.39 | 5.24 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2127
2024-12-18 | 20:04 | 21.9413 | 85.3789 | 3.16 | 3.16 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2128
2024-12-18 | 20:04 | 21.9412 | 85.3788 | 1.39 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 15.1665 | 2129
2024-12-18 | 20:04 | 21.9412 | 85.3788 | 5.24 | 5.24 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2130
2024-12-18 | 20:04 | 21.9412 | 85.3788 | 7.58 | 5.24 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2131
2024-12-18 | 20:04 | 21.9412 | 85.3788 | 10.12 | 3.16 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2132
2024-12-18 | 20:04 | 21.9412 | 85.3788 | 10.12 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2133
2024-12-18 | 20:04 | 21.9412 | 85.3788 | 10.12 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2134
2024-12-18 | 20:04 | 21.9412 | 85.3788 | 10.12 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2135
2024-12-18 | 20:04 | 21.9412 | 85.3788 | 10.12 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2136
2024-12-18 | 20:04 | 21.9412 | 85.3788 | 10.12 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2137
2024-12-18 | 20:04 | 21.9412 | 85.3788 | 10.12 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2138
2024-12-18 | 20:05 | 21.9412 | 85.3788 | 10.12 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2139
2024-12-18 | 20:05 | 21.9412 | 85.3788 | 10.12 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2140
2024-12-18 | 20:05 | 21.9412 | 85.3788 | 10.12 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2141
2024-12-18 | 20:05 | 21.9412 | 85.3788 | 10.12 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2142
2024-12-18 | 20:05 | 21.9412 | 85.3788 | 10.12 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2143
2024-12-18 | 20:05 | 21.9412 | 85.3788 | 10.12 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2144
2024-12-18 | 20:05 | 21.9412 | 85.3788 | 10.12 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2145
2024-12-18 | 20:05 | 21.9412 | 85.3788 | 10.12 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2146
2024-12-18 | 20:05 | 21.9412 | 85.3788 | 10.12 | 3.16 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2147
2024-12-18 | 20:05 | 21.9412 | 85.3788 | 15.57 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2148
2024-12-18 | 20:05 | 21.9412 | 85.3788 | 5.24 | 1.39 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2149
2024-12-18 | 20:05 | 21.9412 | 85.3788 | 3.16 | 0 | 6 | HAUL ROAD (METSO TO KH-1 TRF ROOM) | 0 | 2150
2024-12-18 | 20:05 | 21.9413 | 85.3788 | 5.24 | 5.24 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 11.1192 | 2151
2024-12-18 | 20:05 | 21.9413 | 85.3789 | 7.58 | 7.58 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 10.3144 | 2152
2024-12-18 | 20:05 | 21.9413 | 85.3789 | 1.39 | 7.58 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2153
2024-12-18 | 20:05 | 21.9413 | 85.3789 | 3.16 | 7.58 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2154
2024-12-18 | 20:05 | 21.9413 | 85.3789 | 5.24 | 5.24 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2155
2024-12-18 | 20:05 | 21.9413 | 85.3789 | 1.39 | 3.16 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2156
2024-12-18 | 20:05 | 21.9413 | 85.3789 | 1.39 | 1.39 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2157
2024-12-18 | 20:05 | 21.9414 | 85.379 | 1.39 | 1.39 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 15.1668 | 2158
2024-12-18 | 20:05 | 21.9414 | 85.379 | 1.39 | 3.16 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2159
2024-12-18 | 20:05 | 21.9414 | 85.379 | 1.39 | 3.16 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2160
2024-12-18 | 20:05 | 21.9414 | 85.379 | 1.39 | 10.12 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2161
2024-12-18 | 20:05 | 21.9414 | 85.379 | 7.58 | 10.12 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2162
2024-12-18 | 20:05 | 21.9415 | 85.379 | 3.16 | 5.24 | 19 | MANGLA PARKING | 11.1192 | 2163
2024-12-18 | 20:05 | 21.9415 | 85.379 | 3.16 | 7.58 | 19 | MANGLA PARKING | 0 | 2164
2024-12-18 | 20:05 | 21.9415 | 85.379 | 10.12 | 10.12 | 19 | MANGLA PARKING | 0 | 2165
2024-12-18 | 20:06 | 21.9415 | 85.379 | 7.58 | 12.8 | 19 | MANGLA PARKING | 0 | 2166
2024-12-18 | 20:06 | 21.9415 | 85.379 | 7.58 | 15.57 | 19 | MANGLA PARKING | 0 | 2167
2024-12-18 | 20:06 | 21.9415 | 85.379 | 10.12 | 18.36 | 19 | MANGLA PARKING | 0 | 2168
2024-12-18 | 20:06 | 21.9416 | 85.379 | 10.12 | 21.12 | 19 | MANGLA PARKING | 11.1192 | 2169
2024-12-18 | 20:06 | 21.9416 | 85.379 | 15.57 | 21.12 | 19 | MANGLA PARKING | 0 | 2170
2024-12-18 | 20:06 | 21.9416 | 85.3789 | 15.57 | 26.31 | 19 | MANGLA PARKING | 10.3144 | 2171
2024-12-18 | 20:06 | 21.9416 | 85.3789 | 18.36 | 26.31 | 19 | MANGLA PARKING | 0 | 2172
2024-12-18 | 20:06 | 21.9416 | 85.3789 | 21.12 | 23.79 | 19 | MANGLA PARKING | 0 | 2173
2024-12-18 | 20:06 | 21.9416 | 85.3789 | 21.12 | 30.73 | 19 | MANGLA PARKING | 0 | 2174
2024-12-18 | 20:06 | 21.9417 | 85.3789 | 26.31 | 33.45 | 19 | MANGLA PARKING | 11.1196 | 2175
2024-12-18 | 20:06 | 21.9417 | 85.3789 | 26.31 | 30.73 | 19 | MANGLA PARKING | 0.094935 | 2176
2024-12-18 | 20:06 | 21.9417 | 85.3789 | 38.88 | 30.73 | 19 | MANGLA PARKING | 0.094935 | 2177
2024-12-18 | 20:06 | 21.9417 | 85.3789 | 33.45 | 44.32 | 19 | MANGLA PARKING | 0.094935 | 2178
2024-12-18 | 20:06 | 21.9417 | 85.3789 | 44.32 | 44.32 | 19 | MANGLA PARKING | 0.094935 | 2179
2024-12-18 | 20:06 | 21.9417 | 85.3789 | 36.16 | 38.88 | 19 | MANGLA PARKING | 0.094935 | 2180
2024-12-18 | 20:06 | 21.9417 | 85.3789 | 44.32 | 26.31 | 19 | MANGLA PARKING | 0.094935 | 2181
2024-12-18 | 20:06 | 21.9417 | 85.3789 | 47.04 | 23.79 | 19 | MANGLA PARKING | 0.094935 | 2182
2024-12-18 | 20:06 | 21.9418 | 85.3788 | 44.32 | 18.36 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 15.1665 | 2183
2024-12-18 | 20:06 | 21.9418 | 85.3788 | 60.64 | 26.31 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2184
2024-12-18 | 20:06 | 21.9418 | 85.3788 | 52.48 | 57.92 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2185
2024-12-18 | 20:06 | 21.9418 | 85.3789 | 55.2 | 38.88 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 10.3139 | 2186
2024-12-18 | 20:06 | 21.9418 | 85.3789 | 57.92 | 21.12 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2187
2024-12-18 | 20:06 | 21.9418 | 85.3789 | 49.76 | 18.36 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2188
2024-12-18 | 20:06 | 21.9418 | 85.3789 | 44.32 | 18.36 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2189
2024-12-18 | 20:06 | 21.9418 | 85.3789 | 52.48 | 26.31 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2190
2024-12-18 | 20:06 | 21.9418 | 85.3789 | 60.64 | 33.45 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2191
2024-12-18 | 20:06 | 21.9418 | 85.3789 | 85.14 | 26.31 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2192
2024-12-18 | 20:06 | 21.9418 | 85.379 | 109.68 | 18.36 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 10.3139 | 2193
2024-12-18 | 20:06 | 21.9417 | 85.379 | 112.41 | 5.24 | 9 | MANGLA PARKING PATHWAY | 11.1196 | 2194
2024-12-18 | 20:06 | 21.9417 | 85.379 | 57.92 | 7.58 | 9 | MANGLA PARKING PATHWAY | 0.094935 | 2195
2024-12-18 | 20:07 | 21.9417 | 85.379 | 44.32 | 5.24 | 9 | MANGLA PARKING PATHWAY | 0.094935 | 2196
2024-12-18 | 20:07 | 21.9417 | 85.379 | 7.58 | 15.57 | 9 | MANGLA PARKING PATHWAY | 0.094935 | 2197
2024-12-18 | 20:07 | 21.9417 | 85.379 | 60.64 | 21.12 | 9 | MANGLA PARKING PATHWAY | 0.094935 | 2198
2024-12-18 | 20:07 | 21.9417 | 85.379 | 55.2 | 10.12 | 9 | MANGLA PARKING PATHWAY | 0.094935 | 2199
2024-12-18 | 20:07 | 21.9416 | 85.3791 | 57.92 | 23.79 | 9 | MANGLA PARKING PATHWAY | 15.1668 | 2200
2024-12-18 | 20:07 | 21.9416 | 85.3791 | 79.7 | 30.73 | 9 | MANGLA PARKING PATHWAY | 0 | 2201
2024-12-18 | 20:07 | 21.9416 | 85.3791 | 109.68 | 23.79 | 9 | MANGLA PARKING PATHWAY | 0 | 2202
2024-12-18 | 20:07 | 21.9416 | 85.3791 | 76.97 | 3.16 | 9 | MANGLA PARKING PATHWAY | 0 | 2203
2024-12-18 | 20:07 | 21.9416 | 85.3791 | 76.97 | 5.24 | 9 | MANGLA PARKING PATHWAY | 0 | 2204
2024-12-18 | 20:07 | 21.9416 | 85.3791 | 93.32 | 5.24 | 9 | MANGLA PARKING PATHWAY | 0 | 2205
2024-12-18 | 20:07 | 21.9416 | 85.3791 | 123.33 | 7.58 | 9 | MANGLA PARKING PATHWAY | 0 | 2206
2024-12-18 | 20:07 | 21.9416 | 85.3791 | 126.06 | 71.53 | 9 | MANGLA PARKING PATHWAY | 0 | 2207
2024-12-18 | 20:07 | 21.9417 | 85.3791 | 134.25 | 57.92 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 11.1196 | 2208
2024-12-18 | 20:07 | 21.9417 | 85.3791 | 115.14 | 76.97 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0.094935 | 2209
2024-12-18 | 20:07 | 21.9417 | 85.3791 | 60.64 | 76.97 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0.094935 | 2210
2024-12-18 | 20:07 | 21.9417 | 85.3791 | 33.45 | 123.33 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0.094935 | 2211
2024-12-18 | 20:07 | 21.9417 | 85.379 | 49.76 | 153.39 | 9 | MANGLA PARKING PATHWAY | 10.3144 | 2212
2024-12-18 | 20:07 | 21.9417 | 85.379 | 104.23 | 161.59 | 9 | MANGLA PARKING PATHWAY | 0.094935 | 2213
2024-12-18 | 20:07 | 21.9418 | 85.379 | 142.45 | 172.54 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 11.1196 | 2214
2024-12-18 | 20:07 | 21.9418 | 85.379 | 156.12 | 85.14 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2215
2024-12-18 | 20:07 | 21.9418 | 85.379 | 158.86 | 7.58 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2216
2024-12-18 | 20:07 | 21.9418 | 85.379 | 318.19 | 79.7 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2217
2024-12-18 | 20:07 | 21.9418 | 85.3791 | 356.85 | 21.12 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 10.3139 | 2218
2024-12-18 | 20:07 | 21.9418 | 85.3791 | 147.92 | 36.16 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2219
2024-12-18 | 20:07 | 21.9418 | 85.3791 | 21.12 | 10.12 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2220
2024-12-18 | 20:07 | 21.9418 | 85.3791 | 5.24 | 3.16 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2221
2024-12-18 | 20:07 | 21.9418 | 85.3791 | 0 | 0 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2222
2024-12-18 | 20:07 | 21.9418 | 85.379 | 3.16 | 0 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 10.3139 | 2223
2024-12-18 | 20:07 | 21.9418 | 85.379 | 10.12 | 21.12 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2224
2024-12-18 | 20:07 | 21.9418 | 85.379 | 5.24 | 33.45 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2225
2024-12-18 | 20:08 | 21.9418 | 85.379 | 0 | 7.58 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2226
2024-12-18 | 20:08 | 21.9418 | 85.379 | 0 | 36.16 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2227
2024-12-18 | 20:08 | 21.9418 | 85.379 | 0 | 26.31 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2228
2024-12-18 | 20:08 | 21.9418 | 85.379 | 0 | 0 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2229
2024-12-18 | 20:08 | 21.9418 | 85.379 | 0 | 33.45 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2230
2024-12-18 | 20:08 | 21.9418 | 85.379 | 0 | 5.24 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2231
2024-12-18 | 20:08 | 21.9418 | 85.379 | 0 | 5.24 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2232
2024-12-18 | 20:08 | 21.9418 | 85.379 | 0 | 5.24 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2233
2024-12-18 | 20:08 | 21.9418 | 85.379 | 0 | 5.24 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2234
2024-12-18 | 20:08 | 21.9418 | 85.379 | 0 | 5.24 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2235
2024-12-18 | 20:08 | 21.9418 | 85.379 | 0 | 5.24 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2236
2024-12-18 | 20:08 | 21.9418 | 85.3791 | 0 | 7.58 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 10.3139 | 2237
2024-12-18 | 20:08 | 21.9418 | 85.3791 | 0 | 5.24 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2238
2024-12-18 | 20:08 | 21.9418 | 85.3791 | 0 | 0 | 6 | HAUL ROAD (PB GATE TO OLD EQUIPMENT) | 0 | 2239
2024-12-18 | 20:08 | 21.9418 | 85.3791 | 0 | 3.16 | 6 | HAUL ROAD (OLD EQUIPMENT TO S3) | 0 | 2240
2024-12-18 | 20:08 | 21.9418 | 85.3791 | 0 | 3.16 | 6 | HAUL ROAD (OLD EQUIPMENT TO S3) | 0 | 2241
2024-12-18 | 20:08 | 21.9418 | 85.3791 | 0 | 1.39 | 6 | HAUL ROAD (OLD EQUIPMENT TO S3) | 0 | 2242
2024-12-18 | 20:08 | 21.9418 | 85.3791 | 0 | 1.39 | 6 | HAUL ROAD (OLD EQUIPMENT TO S3) | 0 | 2243
2024-12-18 | 20:08 | 21.9418 | 85.3791 | 0 | 0 | 6 | HAUL ROAD (OLD EQUIPMENT TO S3) | 0 | 2244
2024-12-18 | 20:08 | 21.9418 | 85.3791 | 0 | 5.24 | 6 | HAUL ROAD (OLD EQUIPMENT TO S3) | 0 | 2245
2024-12-18 | 20:08 | 21.9418 | 85.3791 | 0 | 3.16 | 6 | HAUL ROAD (OLD EQUIPMENT TO S3) | 0 | 2246
2024-12-18 | 20:08 | 21.9418 | 85.3791 | 0 | 1.39 | 6 | HAUL ROAD (OLD EQUIPMENT TO S3) | 0 | 2247
2024-12-18 | 20:08 | 21.9418 | 85.3791 | 7.58 | 98.77 | 6 | HAUL ROAD (OLD EQUIPMENT TO S3) | 0 | 2248
2024-12-18 | 20:08 | 21.9418 | 85.3791 | 7.58 | 3.16 | 6 | HAUL ROAD (OLD EQUIPMENT TO S3) | 0 | 2249
2024-12-18 | 20:08 | 21.9418 | 85.3791 | 7.58 | 10.12 | 6 | HAUL ROAD (OLD EQUIPMENT TO S3) | 0 | 2250
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 15.57 | 0 | 4 | HOPPER KH-1 SCREEN PLANT | 55.5974 | 2251
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 30.73 | 0 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2252
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 21.12 | 5.24 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2253
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 30.73 | 0 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2254
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 26.31 | 0 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2255
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 21.12 | 0 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2256
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 23.79 | 7.58 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2257
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 15.57 | 30.73 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2258
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 21.12 | 5.24 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2259
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 36.16 | 5.24 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2260
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 12.8 | 26.31 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2261
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 7.58 | 60.64 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2262
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 7.58 | 44.32 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2263
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 5.24 | 44.32 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2264
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 15.57 | 44.32 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2265
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 15.57 | 47.04 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2266
2024-12-18 | 20:12 | 21.9423 | 85.3791 | 18.36 | 49.76 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2267
2024-12-18 | 20:12 | 21.9423 | 85.379 | 23.79 | 74.25 | 4 | HOPPER KH-1 SCREEN PLANT | 10.3135 | 2268
2024-12-18 | 20:12 | 21.9423 | 85.379 | 26.31 | 33.45 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2269
2024-12-18 | 20:12 | 21.9423 | 85.379 | 33.45 | 52.48 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2270
2024-12-18 | 20:12 | 21.9423 | 85.379 | 33.45 | 68.8 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2271
2024-12-18 | 20:12 | 21.9423 | 85.379 | 30.73 | 79.7 | 4 | HOPPER KH-1 SCREEN PLANT | 0 | 2272
2024-12-18 | 20:12 | 21.9423 | 85.3789 | 30.73 | 87.87 | 6 | HAUL ROAD | 10.3135 | 2273
2024-12-18 | 20:12 | 21.9423 | 85.3789 | 41.6 | 104.23 | 6 | HAUL ROAD | 0 | 2274
2024-12-18 | 20:12 | 21.9423 | 85.3789 | 55.2 | 106.96 | 6 | HAUL ROAD | 0 | 2275
2024-12-18 | 20:13 | 21.9423 | 85.3789 | 38.88 | 134.25 | 6 | HAUL ROAD | 0 | 2276
2024-12-18 | 20:13 | 21.9422 | 85.3789 | 68.8 | 139.72 | 20 | MANGLA CABIN | 11.1192 | 2277
2024-12-18 | 20:13 | 21.9422 | 85.3789 | 55.2 | 158.86 | 20 | MANGLA CABIN | 0 | 2278
2024-12-18 | 20:13 | 21.9422 | 85.3789 | 126.06 | 131.52 | 20 | MANGLA CABIN | 0 | 2279
2024-12-18 | 20:13 | 21.9422 | 85.3789 | 112.41 | 183.49 | 20 | MANGLA CABIN | 0 | 2280
2024-12-18 | 20:13 | 21.9421 | 85.3789 | 142.45 | 85.14 | 13.2 | KH-1 SCREEN PLANT | 11.1196 | 2281
2024-12-18 | 20:13 | 21.9421 | 85.3789 | 150.65 | 123.33 | 13.2 | KH-1 SCREEN PLANT | 0.094935 | 2282
2024-12-18 | 20:13 | 21.9421 | 85.3789 | 139.72 | 167.07 | 13.2 | KH-1 SCREEN PLANT | 0.094935 | 2283
2024-12-18 | 20:13 | 21.9421 | 85.3789 | 117.87 | 142.45 | 13.2 | KH-1 SCREEN PLANT | 0.094935 | 2284
2024-12-18 | 20:13 | 21.9421 | 85.3789 | 112.41 | 85.14 | 13.2 | KH-1 SCREEN PLANT | 0.094935 | 2285
2024-12-18 | 20:13 | 21.9421 | 85.3789 | 98.77 | 15.57 | 13.2 | KH-1 SCREEN PLANT | 0.094935 | 2286
2024-12-18 | 20:13 | 21.942 | 85.3789 | 76.97 | 5.24 | 6 | HAUL ROAD | 11.12 | 2287
2024-12-18 | 20:13 | 21.942 | 85.3789 | 60.64 | 1.39 | 6 | HAUL ROAD | 0 | 2288
2024-12-18 | 20:13 | 21.942 | 85.3789 | 60.64 | 1.39 | 6 | HAUL ROAD | 0 | 2289
2024-12-18 | 20:13 | 21.942 | 85.379 | 63.36 | 5.24 | 6 | HAUL ROAD | 10.3139 | 2290
2024-12-18 | 20:13 | 21.942 | 85.379 | 52.48 | 3.16 | 6 | HAUL ROAD | 0 | 2291
2024-12-18 | 20:13 | 21.9419 | 85.379 | 36.16 | 5.24 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 11.1196 | 2292
2024-12-18 | 20:13 | 21.9419 | 85.379 | 41.6 | 7.58 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 0.094935 | 2293
2024-12-18 | 20:13 | 21.9419 | 85.379 | 1.39 | 3.16 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 0.094935 | 2294
2024-12-18 | 20:13 | 21.9419 | 85.379 | 52.48 | 3.16 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 0.094935 | 2295
2024-12-18 | 20:13 | 21.9419 | 85.379 | 63.36 | 1.39 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 0.094935 | 2296
2024-12-18 | 20:13 | 21.9419 | 85.3791 | 52.48 | 3.16 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 10.3144 | 2297
2024-12-18 | 20:13 | 21.9419 | 85.3791 | 76.97 | 12.8 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 0.094935 | 2298
2024-12-18 | 20:13 | 21.9419 | 85.3791 | 90.59 | 79.7 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 0.094935 | 2299
2024-12-18 | 20:13 | 21.9419 | 85.3791 | 96.05 | 74.25 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 0.094935 | 2300
2024-12-18 | 20:13 | 21.9419 | 85.3791 | 85.14 | 85.14 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 0.094935 | 2301
2024-12-18 | 20:13 | 21.9419 | 85.3791 | 76.97 | 96.05 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 0.094935 | 2302
2024-12-18 | 20:13 | 21.9419 | 85.3791 | 96.05 | 71.53 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 0.094935 | 2303
2024-12-18 | 20:13 | 21.9419 | 85.3792 | 66.08 | 90.59 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 10.3144 | 2304
2024-12-18 | 20:13 | 21.9419 | 85.3792 | 66.08 | 38.88 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 0.094935 | 2305
2024-12-18 | 20:14 | 21.9419 | 85.3792 | 60.64 | 60.64 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 0.094935 | 2306
2024-12-18 | 20:14 | 21.9419 | 85.3792 | 76.97 | 63.36 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 0.094935 | 2307
2024-12-18 | 20:14 | 21.9419 | 85.3792 | 71.53 | 60.64 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 0.094935 | 2308
2024-12-18 | 20:14 | 21.9419 | 85.3792 | 55.2 | 82.42 | 12.2 | BC-1, BC-2, BC-4 (CONVEYOR) | 0.094935 | 2309
2024-12-18 | 20:14 | 21.9418 | 85.3792 | 52.48 | 85.14 | 6 | HAUL ROAD | 11.1196 | 2310
2024-12-18 | 20:14 | 21.9418 | 85.3792 | 74.25 | 112.41 | 6 | HAUL ROAD | 0 | 2311
2024-12-18 | 20:14 | 21.9418 | 85.3792 | 71.53 | 66.08 | 6 | HAUL ROAD | 0 | 2312
2024-12-18 | 20:14 | 21.9418 | 85.3792 | 47.04 | 0 | 6 | HAUL ROAD | 0 | 2313
2024-12-18 | 20:14 | 21.9418 | 85.3792 | 36.16 | 0 | 6 | HAUL ROAD | 0 | 2314
2024-12-18 | 20:14 | 21.9418 | 85.3792 | 23.79 | 0 | 6 | HAUL ROAD | 0 | 2315
2024-12-18 | 20:14 | 21.9418 | 85.3792 | 36.16 | 0 | 6 | HAUL ROAD | 0 | 2316
2024-12-18 | 20:14 | 21.9418 | 85.3792 | 23.79 | 1.39 | 6 | HAUL ROAD | 0 | 2317
2024-12-18 | 20:14 | 21.9418 | 85.3793 | 18.36 | 1.39 | 6 | HAUL ROAD | 10.3139 | 2318
2024-12-18 | 20:14 | 21.9418 | 85.3793 | 10.12 | 5.24 | 6 | HAUL ROAD | 0 | 2319
2024-12-18 | 20:14 | 21.9418 | 85.3793 | 15.57 | 3.16 | 6 | HAUL ROAD | 0 | 2320
2024-12-18 | 20:14 | 21.9418 | 85.3793 | 12.8 | 3.16 | 6 | HAUL ROAD | 0 | 2321
2024-12-18 | 20:14 | 21.9418 | 85.3794 | 12.8 | 3.16 | 6 | HAUL ROAD | 10.3139 | 2322
2024-12-18 | 20:14 | 21.9418 | 85.3794 | 7.58 | 7.58 | 6 | HAUL ROAD | 0 | 2323
2024-12-18 | 20:14 | 21.9418 | 85.3794 | 1.39 | 10.12 | 6 | HAUL ROAD | 0 | 2324
2024-12-18 | 20:14 | 21.9419 | 85.3794 | 7.58 | 7.58 | 6 | HAUL ROAD | 11.1196 | 2325
2024-12-18 | 20:14 | 21.9419 | 85.3794 | 5.24 | 10.12 | 6 | HAUL ROAD | 0.094935 | 2326
2024-12-18 | 20:14 | 21.9419 | 85.3794 | 5.24 | 7.58 | 6 | HAUL ROAD | 0.094935 | 2327
2024-12-18 | 20:14 | 21.9419 | 85.3794 | 5.24 | 12.8 | 6 | HAUL ROAD | 0.094935 | 2328
2024-12-18 | 20:14 | 21.942 | 85.3794 | 5.24 | 12.8 | 6 | HAUL ROAD | 11.1196 | 2329
2024-12-18 | 20:14 | 21.942 | 85.3794 | 7.58 | 10.12 | 6 | HAUL ROAD | 0 | 2330
2024-12-18 | 20:14 | 21.942 | 85.3794 | 10.12 | 18.36 | 6 | HAUL ROAD | 0 | 2331
2024-12-18 | 20:14 | 21.942 | 85.3794 | 12.8 | 12.8 | 6 | HAUL ROAD | 0 | 2332
2024-12-18 | 20:14 | 21.942 | 85.3794 | 12.8 | 26.31 | 6 | HAUL ROAD | 0 | 2333
2024-12-18 | 20:14 | 21.9421 | 85.3794 | 12.8 | 33.45 | 6 | HAUL ROAD | 11.12 | 2334
2024-12-18 | 20:14 | 21.9421 | 85.3793 | 18.36 | 23.79 | 4 | SIZE ORE BC-3 | 10.3144 | 2335
2024-12-18 | 20:15 | 21.9421 | 85.3793 | 18.36 | 33.45 | 4 | SIZE ORE BC-3 | 0.094935 | 2336
2024-12-18 | 20:15 | 21.9421 | 85.3793 | 15.57 | 38.88 | 4 | SIZE ORE BC-3 | 0.094935 | 2337
2024-12-18 | 20:15 | 21.9421 | 85.3793 | 12.8 | 3.16 | 4 | SIZE ORE BC-3 | 0.094935 | 2338
2024-12-18 | 20:15 | 21.9421 | 85.3793 | 15.57 | 41.6 | 4 | SIZE ORE BC-3 | 0.094935 | 2339
2024-12-18 | 20:15 | 21.9421 | 85.3793 | 18.36 | 3.16 | 4 | SIZE ORE BC-3 | 0.094935 | 2340
2024-12-18 | 20:15 | 21.9421 | 85.3793 | 21.12 | 38.88 | 4 | SIZE ORE BC-3 | 0.094935 | 2341
2024-12-18 | 20:15 | 21.9421 | 85.3793 | 18.36 | 41.6 | 4 | SIZE ORE BC-3 | 0.094935 | 2342
2024-12-18 | 20:15 | 21.9421 | 85.3793 | 18.36 | 47.04 | 4 | SIZE ORE BC-3 | 0.094935 | 2343
2024-12-18 | 20:15 | 21.9422 | 85.3794 | 15.57 | 47.04 | 6 | HAUL ROAD | 15.1665 | 2344
2024-12-18 | 20:15 | 21.9422 | 85.3794 | 15.57 | 57.92 | 6 | HAUL ROAD | 0 | 2345
2024-12-18 | 20:15 | 21.9422 | 85.3794 | 18.36 | 60.64 | 6 | HAUL ROAD | 0 | 2346
2024-12-18 | 20:15 | 21.9422 | 85.3794 | 18.36 | 60.64 | 6 | HAUL ROAD | 0 | 2347
2024-12-18 | 20:15 | 21.9422 | 85.3794 | 12.8 | 76.97 | 6 | HAUL ROAD | 0 | 2348
2024-12-18 | 20:15 | 21.9422 | 85.3794 | 12.8 | 63.36 | 6 | HAUL ROAD | 0 | 2349
2024-12-18 | 20:15 | 21.9422 | 85.3794 | 10.12 | 63.36 | 6 | HAUL ROAD | 0 | 2350
2024-12-18 | 20:15 | 21.9422 | 85.3794 | 10.12 | 49.76 | 6 | HAUL ROAD | 0 | 2351
2024-12-18 | 20:15 | 21.9422 | 85.3794 | 10.12 | 26.31 | 6 | HAUL ROAD | 0 | 2352
2024-12-18 | 20:15 | 21.9422 | 85.3794 | 12.8 | 10.12 | 6 | HAUL ROAD | 0 | 2353
2024-12-18 | 20:15 | 21.9422 | 85.3794 | 10.12 | 49.76 | 6 | HAUL ROAD | 0 | 2354
2024-12-18 | 20:15 | 21.9422 | 85.3794 | 15.57 | 76.97 | 6 | HAUL ROAD | 0 | 2355
2024-12-18 | 20:15 | 21.9422 | 85.3794 | 15.57 | 36.16 | 6 | HAUL ROAD | 0 | 2356
2024-12-18 | 20:15 | 21.9421 | 85.3794 | 18.36 | 60.64 | 6 | HAUL ROAD | 11.1196 | 2357
2024-12-18 | 20:15 | 21.9421 | 85.3794 | 15.57 | 41.6 | 6 | HAUL ROAD | 0.094935 | 2358
2024-12-18 | 20:15 | 21.9421 | 85.3794 | 15.57 | 26.31 | 6 | HAUL ROAD | 0.094935 | 2359
2024-12-18 | 20:15 | 21.9421 | 85.3794 | 15.57 | 21.12 | 6 | HAUL ROAD | 0.094935 | 2360
2024-12-18 | 20:15 | 21.9421 | 85.3794 | 12.8 | 26.31 | 6 | HAUL ROAD | 0.094935 | 2361
2024-12-18 | 20:15 | 21.942 | 85.3794 | 12.8 | 15.57 | 6 | HAUL ROAD | 11.12 | 2362
2024-12-18 | 20:15 | 21.942 | 85.3794 | 12.8 | 18.36 | 6 | HAUL ROAD | 0 | 2363
2024-12-18 | 20:15 | 21.942 | 85.3794 | 10.12 | 12.8 | 6 | HAUL ROAD | 0 | 2364
2024-12-18 | 20:15 | 21.942 | 85.3794 | 10.12 | 10.12 | 6 | HAUL ROAD | 0 | 2365
2024-12-18 | 20:16 | 21.942 | 85.3794 | 5.24 | 7.58 | 6 | HAUL ROAD | 0 | 2366
2024-12-18 | 20:16 | 21.942 | 85.3794 | 10.12 | 3.16 | 6 | HAUL ROAD | 0 | 2367
2024-12-18 | 20:16 | 21.9419 | 85.3794 | 7.58 | 1.39 | 6 | HAUL ROAD | 11.1196 | 2368
2024-12-18 | 20:16 | 21.9419 | 85.3794 | 5.24 | 0 | 6 | HAUL ROAD | 0.094935 | 2369
2024-12-18 | 20:16 | 21.9419 | 85.3794 | 3.16 | 0 | 6 | HAUL ROAD | 0.094935 | 2370
2024-12-18 | 20:16 | 21.9419 | 85.3794 | 10.12 | 1.39 | 6 | HAUL ROAD | 0.094935 | 2371
2024-12-18 | 20:16 | 21.9419 | 85.3794 | 3.16 | 0 | 6 | HAUL ROAD | 0.094935 | 2372
2024-12-18 | 20:16 | 21.9418 | 85.3791 | 345.8 | 68.8 | 6 | HAUL ROAD | 32.8796 | 2373
2024-12-18 | 20:16 | 21.9418 | 85.3791 | 387.28 | 21.12 | 6 | HAUL ROAD | 0 | 2374
2024-12-18 | 20:16 | 21.9418 | 85.379 | 164.33 | 12.8 | 6 | HAUL ROAD | 10.3139 | 2375
2024-12-18 | 20:16 | 21.9418 | 85.379 | 96.05 | 10.12 | 6 | HAUL ROAD | 0 | 2376
2024-12-18 | 20:16 | 21.9418 | 85.3791 | 109.68 | 10.12 | 6 | HAUL ROAD | 10.3139 | 2377
2024-12-18 | 20:16 | 21.9418 | 85.3791 | 93.32 | 12.8 | 6 | HAUL ROAD | 0 | 2378
2024-12-18 | 20:17 | 21.9418 | 85.3791 | 98.77 | 18.36 | 6 | HAUL ROAD | 0 | 2379
2024-12-18 | 20:17 | 21.9417 | 85.3791 | 68.8 | 23.79 | 6 | HAUL ROAD | 11.1196 | 2380
2024-12-18 | 20:17 | 21.9417 | 85.3791 | 47.04 | 33.45 | 6 | HAUL ROAD | 0.094935 | 2381
2024-12-18 | 20:17 | 21.9417 | 85.3791 | 87.87 | 26.31 | 6 | HAUL ROAD | 0.094935 | 2382
2024-12-18 | 20:17 | 21.9417 | 85.3791 | 90.59 | 3.16 | 6 | HAUL ROAD | 0.094935 | 2383
2024-12-18 | 20:17 | 21.9417 | 85.3791 | 101.5 | 7.58 | 6 | HAUL ROAD | 0.094935 | 2384
2024-12-18 | 20:17 | 21.9417 | 85.3791 | 104.23 | 3.16 | 6 | HAUL ROAD | 0.094935 | 2385
2024-12-18 | 20:17 | 21.9416 | 85.3791 | 63.36 | 5.24 | 9 | MANGLA PARKING PATHWAY | 11.1196 | 2386
2024-12-18 | 20:17 | 21.9416 | 85.3791 | 96.05 | 7.58 | 9 | MANGLA PARKING PATHWAY | 0 | 2387
2024-12-18 | 20:17 | 21.9416 | 85.3791 | 52.48 | 5.24 | 9 | MANGLA PARKING PATHWAY | 0 | 2388
2024-12-18 | 20:17 | 21.9416 | 85.3791 | 10.12 | 3.16 | 9 | MANGLA PARKING PATHWAY | 0 | 2389
2024-12-18 | 20:17 | 21.9416 | 85.3791 | 41.6 | 0 | 9 | MANGLA PARKING PATHWAY | 0 | 2390
2024-12-18 | 20:17 | 21.9416 | 85.3791 | 1.39 | 1.39 | 9 | MANGLA PARKING PATHWAY | 0 | 2391
2024-12-18 | 20:17 | 21.9415 | 85.379 | 3.16 | 1.39 | 19 | MANGLA PARKING | 15.1665 | 2392
2024-12-18 | 20:17 | 21.9415 | 85.379 | 7.58 | 7.58 | 19 | MANGLA PARKING | 0 | 2393
2024-12-18 | 20:17 | 21.9415 | 85.379 | 1.39 | 5.24 | 19 | MANGLA PARKING | 0 | 2394
2024-12-18 | 20:17 | 21.9415 | 85.379 | 1.39 | 3.16 | 19 | MANGLA PARKING | 0 | 2395
2024-12-18 | 20:17 | 21.9415 | 85.379 | 1.39 | 3.16 | 19 | MANGLA PARKING | 0 | 2396
2024-12-18 | 20:18 | 21.9412 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 39.2213 | 2397
2024-12-18 | 20:18 | 21.9412 | 85.3788 | 5.24 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2398
2024-12-18 | 20:18 | 21.9412 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2399
2024-12-18 | 20:18 | 21.9412 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2400
2024-12-18 | 20:18 | 21.9412 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2401
2024-12-18 | 20:18 | 21.9412 | 85.3788 | 7.58 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2402
2024-12-18 | 20:18 | 21.9412 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2403
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2404
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2405
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2406
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2407
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2408
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2409
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2410
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 10.12 | 3.16 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2411
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 7.58 | 3.16 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2412
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2413
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2414
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2415
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 7.58 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2416
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 7.58 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2417
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 7.58 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2418
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 7.58 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2419
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 7.58 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2420
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 7.58 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2421
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 7.58 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2422
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 7.58 | 5.24 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2423
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 7.58 | 5.24 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2424
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 7.58 | 5.24 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2425
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 7.58 | 5.24 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2426
2024-12-18 | 20:19 | 21.9412 | 85.3788 | 7.58 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2427
2024-12-18 | 20:19 | 21.9413 | 85.3789 | 1.39 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1665 | 2428
2024-12-18 | 20:19 | 21.9412 | 85.3789 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1192 | 2429
2024-12-18 | 20:19 | 21.9412 | 85.379 | 1.39 | 10.12 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2430
2024-12-18 | 20:19 | 21.9411 | 85.3789 | 18.36 | 15.57 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1668 | 2431
2024-12-18 | 20:19 | 21.941 | 85.3789 | 66.08 | 3.16 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1192 | 2432
2024-12-18 | 20:19 | 21.941 | 85.3789 | 33.45 | 5.24 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2433
2024-12-18 | 20:20 | 21.9409 | 85.3789 | 10.12 | 5.24 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2434
2024-12-18 | 20:20 | 21.9409 | 85.3789 | 1.39 | 10.12 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2435
2024-12-18 | 20:20 | 21.9408 | 85.379 | 26.31 | 12.8 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1665 | 2436
2024-12-18 | 20:20 | 21.9408 | 85.379 | 66.08 | 3.16 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2437
2024-12-18 | 20:20 | 21.9407 | 85.3789 | 36.16 | 7.58 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1665 | 2438
2024-12-18 | 20:20 | 21.9407 | 85.3789 | 7.58 | 15.57 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2439
2024-12-18 | 20:20 | 21.9406 | 85.3789 | 5.24 | 26.31 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1192 | 2440
2024-12-18 | 20:20 | 21.9405 | 85.3789 | 23.79 | 30.73 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2441
2024-12-18 | 20:20 | 21.9405 | 85.3789 | 44.32 | 5.24 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0.094935 | 2442
2024-12-18 | 20:20 | 21.9405 | 85.3788 | 3.16 | 5.24 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3148 | 2443
2024-12-18 | 20:20 | 21.9404 | 85.3788 | 0 | 3.16 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2444
2024-12-18 | 20:20 | 21.9404 | 85.3787 | 0 | 7.58 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2445
2024-12-18 | 20:20 | 21.9403 | 85.3786 | 0 | 7.58 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1668 | 2446
2024-12-18 | 20:20 | 21.9402 | 85.3786 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2447
2024-12-18 | 20:20 | 21.9402 | 85.3785 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3139 | 2448
2024-12-18 | 20:20 | 21.9401 | 85.3784 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1668 | 2449
2024-12-18 | 20:20 | 21.94 | 85.3783 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1665 | 2450
2024-12-18 | 20:20 | 21.9399 | 85.3783 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1192 | 2451
2024-12-18 | 20:20 | 21.9399 | 85.3782 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2452
2024-12-18 | 20:20 | 21.9398 | 85.3781 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1665 | 2453
2024-12-18 | 20:20 | 21.9398 | 85.3781 | 1.39 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2454
2024-12-18 | 20:20 | 21.9398 | 85.378 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2455
2024-12-18 | 20:20 | 21.9397 | 85.378 | 1.39 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2456
2024-12-18 | 20:20 | 21.9397 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3148 | 2457
2024-12-18 | 20:20 | 21.9397 | 85.3779 | 3.16 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0.094935 | 2458
2024-12-18 | 20:20 | 21.9396 | 85.3779 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2459
2024-12-18 | 20:20 | 21.9396 | 85.3778 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2460
2024-12-18 | 20:20 | 21.9395 | 85.3778 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2461
2024-12-18 | 20:20 | 21.9395 | 85.3778 | 0 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0.094935 | 2462
2024-12-18 | 20:20 | 21.9394 | 85.3777 | 1.39 | 3.16 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1671 | 2463
2024-12-18 | 20:21 | 21.9393 | 85.3777 | 1.39 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1192 | 2464
2024-12-18 | 20:21 | 21.9392 | 85.3777 | 21.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2465
2024-12-18 | 20:21 | 21.9391 | 85.3777 | 5.24 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2466
2024-12-18 | 20:21 | 21.939 | 85.3777 | 7.58 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1192 | 2467
2024-12-18 | 20:21 | 21.939 | 85.3777 | 15.57 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2468
2024-12-18 | 20:21 | 21.9389 | 85.3777 | 3.16 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1192 | 2469
2024-12-18 | 20:21 | 21.9387 | 85.3777 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 22.239 | 2470
2024-12-18 | 20:21 | 21.9386 | 85.3777 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2471
2024-12-18 | 20:21 | 21.9385 | 85.3776 | 1.39 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1671 | 2472
2024-12-18 | 20:21 | 21.9384 | 85.3776 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2473
2024-12-18 | 20:21 | 21.9383 | 85.3776 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1192 | 2474
2024-12-18 | 20:21 | 21.9383 | 85.3776 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2475
2024-12-18 | 20:21 | 21.9382 | 85.3776 | 10.12 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1192 | 2476
2024-12-18 | 20:21 | 21.9381 | 85.3776 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2477
2024-12-18 | 20:21 | 21.938 | 85.3776 | 3.16 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2478
2024-12-18 | 20:21 | 21.9379 | 85.3776 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2479
2024-12-18 | 20:21 | 21.9377 | 85.3776 | 3.16 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 22.239 | 2480
2024-12-18 | 20:21 | 21.9376 | 85.3776 | 0 | 7.58 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2481
2024-12-18 | 20:21 | 21.9375 | 85.3776 | 12.8 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.12 | 2482
2024-12-18 | 20:21 | 21.9374 | 85.3776 | 3.16 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.12 | 2483
2024-12-18 | 20:21 | 21.9373 | 85.3776 | 7.58 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2484
2024-12-18 | 20:21 | 21.9372 | 85.3776 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.12 | 2485
2024-12-18 | 20:21 | 21.9371 | 85.3776 | 3.16 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2486
2024-12-18 | 20:21 | 21.937 | 85.3776 | 1.39 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2487
2024-12-18 | 20:21 | 21.9368 | 85.3776 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 22.2388 | 2488
2024-12-18 | 20:21 | 21.9368 | 85.3776 | 1.39 | 3.16 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2489
2024-12-18 | 20:21 | 21.9367 | 85.3776 | 3.16 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1192 | 2490
2024-12-18 | 20:21 | 21.9366 | 85.3777 | 0 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1668 | 2491
2024-12-18 | 20:21 | 21.9366 | 85.3777 | 0 | 3.16 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2492
2024-12-18 | 20:21 | 21.9365 | 85.3777 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2493
2024-12-18 | 20:22 | 21.9364 | 85.3777 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2494
2024-12-18 | 20:22 | 21.9364 | 85.3777 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2495
2024-12-18 | 20:22 | 21.9363 | 85.3777 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2496
2024-12-18 | 20:22 | 21.9363 | 85.3777 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2497
2024-12-18 | 20:22 | 21.9362 | 85.3778 | 0 | 3.16 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1665 | 2498
2024-12-18 | 20:22 | 21.9362 | 85.3778 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2499
2024-12-18 | 20:22 | 21.9362 | 85.3778 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2500
2024-12-18 | 20:22 | 21.9361 | 85.3779 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1665 | 2501
2024-12-18 | 20:22 | 21.9361 | 85.378 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2502
2024-12-18 | 20:22 | 21.9361 | 85.3781 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2503
2024-12-18 | 20:22 | 21.9361 | 85.3781 | 0 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2504
2024-12-18 | 20:22 | 21.9361 | 85.3782 | 0 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2505
2024-12-18 | 20:22 | 21.936 | 85.3783 | 3.16 | 3.16 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1668 | 2506
2024-12-18 | 20:22 | 21.936 | 85.3783 | 21.12 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2507
2024-12-18 | 20:22 | 21.936 | 85.3784 | 12.8 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2508
2024-12-18 | 20:22 | 21.936 | 85.3785 | 5.24 | 15.57 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2509
2024-12-18 | 20:22 | 21.9359 | 85.3786 | 57.92 | 5.24 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1668 | 2510
2024-12-18 | 20:22 | 21.9359 | 85.3787 | 15.57 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2511
2024-12-18 | 20:22 | 21.9359 | 85.3788 | 0 | 5.24 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2512
2024-12-18 | 20:22 | 21.9359 | 85.3789 | 10.12 | 23.79 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2513
2024-12-18 | 20:22 | 21.9359 | 85.3789 | 142.45 | 15.57 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2514
2024-12-18 | 20:22 | 21.9359 | 85.379 | 44.32 | 5.24 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2515
2024-12-18 | 20:22 | 21.9359 | 85.3791 | 33.45 | 26.31 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2516
2024-12-18 | 20:22 | 21.9359 | 85.3792 | 93.32 | 5.24 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2517
2024-12-18 | 20:22 | 21.9359 | 85.3792 | 12.8 | 3.16 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2518
2024-12-18 | 20:22 | 21.9359 | 85.3793 | 0 | 7.58 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2519
2024-12-18 | 20:22 | 21.9359 | 85.3794 | 1.39 | 10.12 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2520
2024-12-18 | 20:22 | 21.9359 | 85.3794 | 3.16 | 10.12 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2521
2024-12-18 | 20:22 | 21.9359 | 85.3795 | 10.12 | 10.12 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2522
2024-12-18 | 20:22 | 21.936 | 85.3796 | 15.57 | 7.58 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1668 | 2523
2024-12-18 | 20:23 | 21.936 | 85.3796 | 18.36 | 3.16 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2524
2024-12-18 | 20:23 | 21.936 | 85.3797 | 23.79 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2525
2024-12-18 | 20:23 | 21.9361 | 85.3797 | 36.16 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2526
2024-12-18 | 20:23 | 21.9361 | 85.3798 | 60.64 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2527
2024-12-18 | 20:23 | 21.9361 | 85.3799 | 57.92 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 10.3144 | 2528
2024-12-18 | 20:23 | 21.936 | 85.38 | 60.64 | 1.39 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1668 | 2529
2024-12-18 | 20:23 | 21.936 | 85.38 | 76.97 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2530
2024-12-18 | 20:23 | 21.9359 | 85.3801 | 82.42 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1668 | 2531
2024-12-18 | 20:23 | 21.9358 | 85.3801 | 90.59 | 5.24 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1192 | 2532
2024-12-18 | 20:23 | 21.9357 | 85.3802 | 112.41 | 7.58 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1665 | 2533
2024-12-18 | 20:23 | 21.9357 | 85.3802 | 82.42 | 18.36 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2534
2024-12-18 | 20:23 | 21.9356 | 85.3802 | 57.92 | 0 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 11.1196 | 2535
2024-12-18 | 20:23 | 21.9355 | 85.3803 | 23.79 | 3.16 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 15.1671 | 2536
2024-12-18 | 20:23 | 21.9355 | 85.3803 | 15.57 | 10.12 | 6 | HAUL ROAD (KH-1 IRC TO PB GATE) | 0 | 2537
2024-12-18 | 20:23 | 21.9354 | 85.3803 | 33.45 | 3.16 | 6 | HAUL ROAD | 11.1196 | 2538
2024-12-18 | 20:23 | 21.9354 | 85.3803 | 26.31 | 15.57 | 6 | HAUL ROAD | 0.094935 | 2539
2024-12-18 | 20:23 | 21.9354 | 85.3803 | 106.96 | 5.24 | 6 | HAUL ROAD | 0.094935 | 2540
2024-12-18 | 20:23 | 21.9353 | 85.3804 | 90.59 | 10.12 | 6 | HAUL ROAD | 15.1671 | 2541
2024-12-18 | 20:23 | 21.9353 | 85.3804 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 2542
2024-12-18 | 20:23 | 21.9352 | 85.3804 | 5.24 | 38.88 | 6 | HAUL ROAD | 11.1192 | 2543
2024-12-18 | 20:23 | 21.9351 | 85.3805 | 21.12 | 44.32 | 6 | HAUL ROAD | 15.1668 | 2544
2024-12-18 | 20:23 | 21.9351 | 85.3805 | 44.32 | 44.32 | 6 | HAUL ROAD | 0 | 2545
2024-12-18 | 20:23 | 21.935 | 85.3805 | 44.32 | 18.36 | 6 | HAUL ROAD | 11.1192 | 2546
2024-12-18 | 20:23 | 21.935 | 85.3806 | 0 | 1.39 | 6 | HAUL ROAD | 10.3148 | 2547
2024-12-18 | 20:23 | 21.9349 | 85.3807 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 2548
2024-12-18 | 20:23 | 21.9349 | 85.3807 | 0 | 5.24 | 6 | HAUL ROAD | 0.094935 | 2549
2024-12-18 | 20:23 | 21.9349 | 85.3808 | 3.16 | 15.57 | 6 | HAUL ROAD | 10.3152 | 2550
2024-12-18 | 20:23 | 21.9348 | 85.3809 | 26.31 | 26.31 | 6 | HAUL ROAD | 15.1674 | 2551
2024-12-18 | 20:23 | 21.9348 | 85.381 | 55.2 | 0 | 6 | HAUL ROAD | 10.3152 | 2552
2024-12-18 | 20:23 | 21.9348 | 85.3811 | 1.39 | 3.16 | 6 | HAUL ROAD | 10.3152 | 2553
2024-12-18 | 20:24 | 21.9348 | 85.3812 | 0 | 5.24 | 6 | HAUL ROAD | 10.3152 | 2554
2024-12-18 | 20:24 | 21.9348 | 85.3813 | 10.12 | 15.57 | 6 | HAUL ROAD | 10.3152 | 2555
2024-12-18 | 20:24 | 21.9348 | 85.3815 | 71.53 | 0 | 6 | HAUL ROAD | 20.6292 | 2556
2024-12-18 | 20:24 | 21.9347 | 85.3815 | 1.39 | 0 | 6 | HAUL ROAD | 11.1196 | 2557
2024-12-18 | 20:24 | 21.9346 | 85.3815 | 1.39 | 1.39 | 6 | HAUL ROAD | 11.1192 | 2558
2024-12-18 | 20:24 | 21.9345 | 85.3815 | 0 | 1.39 | 6 | HAUL ROAD | 11.1192 | 2559
2024-12-18 | 20:24 | 21.9345 | 85.3814 | 1.39 | 3.16 | 6 | HAUL ROAD | 10.3144 | 2560
2024-12-18 | 20:24 | 21.9344 | 85.3813 | 26.31 | 0 | 6 | HAUL ROAD | 15.1671 | 2561
2024-12-18 | 20:24 | 21.9343 | 85.3813 | 1.39 | 0 | 6 | HAUL ROAD | 11.1192 | 2562
2024-12-18 | 20:24 | 21.9342 | 85.3812 | 5.24 | 1.39 | 6 | HAUL ROAD | 15.1668 | 2563
2024-12-18 | 20:24 | 21.9341 | 85.3811 | 10.12 | 0 | 6 | HAUL ROAD | 15.1671 | 2564
2024-12-18 | 20:24 | 21.9341 | 85.381 | 0 | 0 | 6 | HAUL ROAD | 10.3144 | 2565
2024-12-18 | 20:24 | 21.934 | 85.3809 | 10.12 | 3.16 | 6 | HAUL ROAD | 15.1668 | 2566
2024-12-18 | 20:24 | 21.9339 | 85.3808 | 7.58 | 0 | 6 | HAUL ROAD | 15.1671 | 2567
2024-12-18 | 20:24 | 21.9338 | 85.3807 | 0 | 0 | 6 | HAUL ROAD | 15.1668 | 2568
2024-12-18 | 20:24 | 21.9337 | 85.3806 | 12.8 | 1.39 | 6 | HAUL ROAD | 15.1671 | 2569
2024-12-18 | 20:24 | 21.9336 | 85.3806 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 2570
2024-12-18 | 20:24 | 21.9336 | 85.3805 | 3.16 | 5.24 | 6 | HAUL ROAD | 10.3148 | 2571
2024-12-18 | 20:24 | 21.9335 | 85.3804 | 12.8 | 1.39 | 6 | HAUL ROAD | 15.1668 | 2572
2024-12-18 | 20:24 | 21.9334 | 85.3803 | 0 | 0 | 6 | HAUL ROAD | 15.1668 | 2573
2024-12-18 | 20:24 | 21.9333 | 85.3802 | 7.58 | 0 | 6 | HAUL ROAD | 15.1671 | 2574
2024-12-18 | 20:24 | 21.9332 | 85.3801 | 1.39 | 0 | 6 | HAUL ROAD | 15.1671 | 2575
2024-12-18 | 20:24 | 21.9331 | 85.3801 | 3.16 | 3.16 | 6 | HAUL ROAD | 11.1196 | 2576
2024-12-18 | 20:24 | 21.933 | 85.38 | 23.79 | 0 | 6 | HAUL ROAD | 15.1671 | 2577
2024-12-18 | 20:24 | 21.9329 | 85.3799 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 2578
2024-12-18 | 20:24 | 21.9328 | 85.3798 | 7.58 | 3.16 | 6 | HAUL ROAD | 15.1671 | 2579
2024-12-18 | 20:24 | 21.9327 | 85.3798 | 15.57 | 0 | 6 | HAUL ROAD | 11.1192 | 2580
2024-12-18 | 20:24 | 21.9327 | 85.3797 | 0 | 3.16 | 6 | HAUL ROAD | 10.3148 | 2581
2024-12-18 | 20:24 | 21.9326 | 85.3797 | 1.39 | 10.12 | 6 | HAUL ROAD | 11.1192 | 2582
2024-12-18 | 20:24 | 21.9325 | 85.3797 | 30.73 | 7.58 | 6 | HAUL ROAD | 11.1196 | 2583
2024-12-18 | 20:25 | 21.9324 | 85.3796 | 15.57 | 5.24 | 6 | HAUL ROAD | 15.1671 | 2584
2024-12-18 | 20:25 | 21.9323 | 85.3796 | 5.24 | 10.12 | 6 | HAUL ROAD | 11.1196 | 2585
2024-12-18 | 20:25 | 21.9323 | 85.3796 | 7.58 | 7.58 | 6 | HAUL ROAD | 0.094935 | 2586
2024-12-18 | 20:25 | 21.9322 | 85.3796 | 12.8 | 7.58 | 6 | HAUL ROAD | 11.12 | 2587
2024-12-18 | 20:25 | 21.9321 | 85.3796 | 15.57 | 7.58 | 6 | HAUL ROAD | 11.1196 | 2588
2024-12-18 | 20:25 | 21.9321 | 85.3796 | 7.58 | 10.12 | 6 | HAUL ROAD | 0.094935 | 2589
2024-12-18 | 20:25 | 21.932 | 85.3796 | 7.58 | 12.8 | 6 | HAUL ROAD | 11.1196 | 2590
2024-12-18 | 20:25 | 21.932 | 85.3796 | 7.58 | 18.36 | 6 | HAUL ROAD | 0 | 2591
2024-12-18 | 20:25 | 21.9319 | 85.3796 | 7.58 | 21.12 | 6 | HAUL ROAD | 11.1196 | 2592
2024-12-18 | 20:25 | 21.9318 | 85.3796 | 10.12 | 18.36 | 6 | HAUL ROAD | 11.1196 | 2593
2024-12-18 | 20:25 | 21.9318 | 85.3796 | 15.57 | 18.36 | 6 | HAUL ROAD | 0 | 2594
2024-12-18 | 20:25 | 21.9317 | 85.3796 | 21.12 | 10.12 | 6 | HAUL ROAD | 11.1196 | 2595
2024-12-18 | 20:25 | 21.9316 | 85.3796 | 26.31 | 7.58 | 6 | HAUL ROAD | 11.1196 | 2596
2024-12-18 | 20:25 | 21.9314 | 85.3797 | 23.79 | 7.58 | 6 | HAUL ROAD | 24.5146 | 2597
2024-12-18 | 20:25 | 21.9313 | 85.3797 | 12.8 | 5.24 | 6 | HAUL ROAD | 11.1196 | 2598
2024-12-18 | 20:25 | 21.9312 | 85.3798 | 3.16 | 7.58 | 6 | HAUL ROAD | 15.1671 | 2599
2024-12-18 | 20:25 | 21.9311 | 85.3798 | 5.24 | 5.24 | 6 | HAUL ROAD | 11.1196 | 2600
2024-12-18 | 20:25 | 21.931 | 85.3799 | 1.39 | 10.12 | 6 | HAUL ROAD | 15.1671 | 2601
2024-12-18 | 20:25 | 21.9309 | 85.38 | 1.39 | 5.24 | 6 | HAUL ROAD | 15.1671 | 2602
2024-12-18 | 20:25 | 21.9308 | 85.38 | 0 | 7.58 | 6 | HAUL ROAD | 11.12 | 2603
2024-12-18 | 20:25 | 21.9307 | 85.3801 | 0 | 5.24 | 6 | HAUL ROAD | 15.1671 | 2604
2024-12-18 | 20:25 | 21.9306 | 85.3802 | 0 | 1.39 | 6 | HAUL ROAD | 15.1671 | 2605
2024-12-18 | 20:25 | 21.9305 | 85.3802 | 0 | 5.24 | 6 | HAUL ROAD | 11.1192 | 2606
2024-12-18 | 20:25 | 21.9304 | 85.3803 | 0 | 10.12 | 6 | HAUL ROAD | 15.1671 | 2607
2024-12-18 | 20:25 | 21.9303 | 85.3803 | 1.39 | 10.12 | 6 | HAUL ROAD | 11.1192 | 2608
2024-12-18 | 20:25 | 21.9302 | 85.3804 | 0 | 12.8 | 6 | HAUL ROAD | 15.1671 | 2609
2024-12-18 | 20:25 | 21.9301 | 85.3805 | 1.39 | 21.12 | 6 | HAUL ROAD | 15.1671 | 2610
2024-12-18 | 20:25 | 21.9301 | 85.3806 | 10.12 | 30.73 | 6 | HAUL ROAD | 10.3152 | 2611
2024-12-18 | 20:25 | 21.93 | 85.3807 | 44.32 | 44.32 | 6 | HAUL ROAD | 15.1671 | 2612
2024-12-18 | 20:25 | 21.9299 | 85.3808 | 85.14 | 30.73 | 6 | HAUL ROAD | 15.1671 | 2613
2024-12-18 | 20:26 | 21.9299 | 85.3809 | 18.36 | 7.58 | 6 | HAUL ROAD | 10.3152 | 2614
2024-12-18 | 20:26 | 21.9298 | 85.3809 | 30.73 | 10.12 | 6 | HAUL ROAD | 11.12 | 2615
2024-12-18 | 20:26 | 21.9297 | 85.381 | 21.12 | 3.16 | 6 | HAUL ROAD | 15.1671 | 2616
2024-12-18 | 20:26 | 21.9297 | 85.3811 | 12.8 | 1.39 | 6 | HAUL ROAD | 10.3148 | 2617
2024-12-18 | 20:26 | 21.9296 | 85.3811 | 3.16 | 0 | 6 | HAUL ROAD | 11.1192 | 2618
2024-12-18 | 20:26 | 21.9296 | 85.3812 | 0 | 0 | 6 | HAUL ROAD | 10.3148 | 2619
2024-12-18 | 20:26 | 21.9295 | 85.3813 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 2620
2024-12-18 | 20:26 | 21.9294 | 85.3814 | 0 | 0 | 6 | HAUL ROAD | 15.1674 | 2621
2024-12-18 | 20:26 | 21.9293 | 85.3814 | 1.39 | 3.16 | 6 | HAUL ROAD | 11.1196 | 2622
2024-12-18 | 20:26 | 21.9293 | 85.3814 | 1.39 | 0 | 6 | HAUL ROAD | 0 | 2623
2024-12-18 | 20:26 | 21.9292 | 85.3814 | 3.16 | 3.16 | 6 | HAUL ROAD | 11.1192 | 2624
2024-12-18 | 20:26 | 21.9292 | 85.3814 | 5.24 | 3.16 | 6 | HAUL ROAD | 0 | 2625
2024-12-18 | 20:26 | 21.9291 | 85.3814 | 10.12 | 5.24 | 6 | HAUL ROAD | 11.1196 | 2626
2024-12-18 | 20:26 | 21.9291 | 85.3813 | 18.36 | 10.12 | 6 | HAUL ROAD | 10.3148 | 2627
2024-12-18 | 20:26 | 21.929 | 85.3813 | 21.12 | 15.57 | 6 | HAUL ROAD | 11.1192 | 2628
2024-12-18 | 20:26 | 21.929 | 85.3812 | 21.12 | 21.12 | 6 | HAUL ROAD | 10.3148 | 2629
2024-12-18 | 20:26 | 21.9289 | 85.3811 | 21.12 | 12.8 | 6 | HAUL ROAD | 15.1674 | 2630
2024-12-18 | 20:26 | 21.9288 | 85.381 | 87.87 | 3.16 | 6 | HAUL ROAD | 15.1671 | 2631
2024-12-18 | 20:26 | 21.9288 | 85.381 | 44.32 | 3.16 | 6 | HAUL ROAD | 0 | 2632
2024-12-18 | 20:26 | 21.9287 | 85.3809 | 12.8 | 7.58 | 6 | HAUL ROAD | 15.1671 | 2633
2024-12-18 | 20:26 | 21.9286 | 85.3808 | 47.04 | 0 | 6 | HAUL ROAD | 15.1674 | 2634
2024-12-18 | 20:26 | 21.9286 | 85.3807 | 3.16 | 0 | 6 | HAUL ROAD | 10.3152 | 2635
2024-12-18 | 20:26 | 21.9285 | 85.3806 | 1.39 | 5.24 | 6 | HAUL ROAD | 15.1674 | 2636
2024-12-18 | 20:26 | 21.9285 | 85.3806 | 26.31 | 12.8 | 6 | HAUL ROAD | 0 | 2637
2024-12-18 | 20:26 | 21.9284 | 85.3805 | 41.6 | 0 | 6 | HAUL ROAD | 15.1671 | 2638
2024-12-18 | 20:26 | 21.9283 | 85.3805 | 3.16 | 0 | 6 | HAUL ROAD | 11.1196 | 2639
2024-12-18 | 20:26 | 21.9283 | 85.3804 | 1.39 | 3.16 | 6 | HAUL ROAD | 10.3152 | 2640
2024-12-18 | 20:26 | 21.9282 | 85.3803 | 23.79 | 0 | 6 | HAUL ROAD | 15.1671 | 2641
2024-12-18 | 20:26 | 21.9281 | 85.3803 | 7.58 | 3.16 | 6 | HAUL ROAD | 11.1192 | 2642
2024-12-18 | 20:26 | 21.9281 | 85.3802 | 12.8 | 1.39 | 6 | HAUL ROAD | 10.3148 | 2643
2024-12-18 | 20:27 | 21.9281 | 85.3801 | 1.39 | 3.16 | 6 | HAUL ROAD | 10.3148 | 2644
2024-12-18 | 20:27 | 21.928 | 85.3801 | 0 | 5.24 | 6 | HAUL ROAD | 11.1192 | 2645
2024-12-18 | 20:27 | 21.928 | 85.38 | 0 | 10.12 | 6 | HAUL ROAD | 10.3152 | 2646
2024-12-18 | 20:27 | 21.928 | 85.3799 | 3.16 | 23.79 | 6 | HAUL ROAD | 10.3152 | 2647
2024-12-18 | 20:27 | 21.9281 | 85.3799 | 21.12 | 44.32 | 6 | HAUL ROAD | 11.1192 | 2648
2024-12-18 | 20:27 | 21.9281 | 85.3798 | 66.08 | 49.76 | 6 | HAUL ROAD | 10.3148 | 2649
2024-12-18 | 20:27 | 21.9281 | 85.3798 | 161.59 | 0 | 6 | HAUL ROAD | 0 | 2650
2024-12-18 | 20:27 | 21.9282 | 85.3797 | 47.04 | 1.39 | 6 | HAUL ROAD | 15.1671 | 2651
2024-12-18 | 20:27 | 21.9283 | 85.3797 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 2652
2024-12-18 | 20:27 | 21.9283 | 85.3797 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 2653
2024-12-18 | 20:27 | 21.9284 | 85.3796 | 0 | 3.16 | 6 | HAUL ROAD | 15.1674 | 2654
2024-12-18 | 20:27 | 21.9284 | 85.3796 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 2655
2024-12-18 | 20:27 | 21.9284 | 85.3796 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 2656
2024-12-18 | 20:27 | 21.9285 | 85.3796 | 1.39 | 3.16 | 6 | HAUL ROAD | 11.1192 | 2657
2024-12-18 | 20:27 | 21.9285 | 85.3796 | 5.24 | 5.24 | 6 | HAUL ROAD | 0 | 2658
2024-12-18 | 20:27 | 21.9286 | 85.3795 | 10.12 | 12.8 | 6 | HAUL ROAD | 15.1674 | 2659
2024-12-18 | 20:27 | 21.9287 | 85.3795 | 41.6 | 36.16 | 6 | HAUL ROAD | 11.1196 | 2660
2024-12-18 | 20:27 | 21.9287 | 85.3795 | 126.06 | 63.36 | 6 | HAUL ROAD | 0.094935 | 2661
2024-12-18 | 20:27 | 21.9288 | 85.3794 | 238.36 | 60.64 | 6 | HAUL ROAD | 15.1671 | 2662
2024-12-18 | 20:27 | 21.9288 | 85.3794 | 395.59 | 5.24 | 6 | HAUL ROAD | 0 | 2663
2024-12-18 | 20:27 | 21.9288 | 85.3793 | 340.27 | 0 | 4 | S3 STOCK | 10.3148 | 2664
2024-12-18 | 20:27 | 21.9289 | 85.3792 | 123.33 | 0 | 4 | S3 STOCK | 15.1671 | 2665
2024-12-18 | 20:27 | 21.9289 | 85.3792 | 55.2 | 0 | 4 | S3 STOCK | 0 | 2666
2024-12-18 | 20:27 | 21.9289 | 85.3791 | 36.16 | 0 | 6 | HAUL ROAD | 10.3152 | 2667
2024-12-18 | 20:27 | 21.9289 | 85.379 | 1.39 | 0 | 6 | HAUL ROAD | 10.3152 | 2668
2024-12-18 | 20:27 | 21.9289 | 85.379 | 0 | 0 | 6 | HAUL ROAD | 0 | 2669
2024-12-18 | 20:27 | 21.9288 | 85.3789 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 2670
2024-12-18 | 20:27 | 21.9287 | 85.379 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 2671
2024-12-18 | 20:27 | 21.9287 | 85.379 | 0 | 1.39 | 6 | HAUL ROAD | 0.094935 | 2672
2024-12-18 | 20:27 | 21.9287 | 85.3791 | 1.39 | 21.12 | 6 | HAUL ROAD | 10.3157 | 2673
2024-12-18 | 20:28 | 21.9287 | 85.3792 | 18.36 | 55.2 | 4 | S3 STOCK | 10.3157 | 2674
2024-12-18 | 20:28 | 21.9287 | 85.3793 | 60.64 | 82.42 | 4 | S3 STOCK | 10.3157 | 2675
2024-12-18 | 20:28 | 21.9286 | 85.3793 | 66.08 | 33.45 | 6 | HAUL ROAD | 11.1196 | 2676
2024-12-18 | 20:28 | 21.9286 | 85.3794 | 49.76 | 0 | 6 | HAUL ROAD | 10.3152 | 2677
2024-12-18 | 20:28 | 21.9285 | 85.3795 | 26.31 | 3.16 | 6 | HAUL ROAD | 15.1674 | 2678
2024-12-18 | 20:28 | 21.9285 | 85.3795 | 5.24 | 1.39 | 6 | HAUL ROAD | 0 | 2679
2024-12-18 | 20:28 | 21.9284 | 85.3796 | 0 | 1.39 | 6 | HAUL ROAD | 15.1671 | 2680
2024-12-18 | 20:28 | 21.9284 | 85.3796 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 2681
2024-12-18 | 20:28 | 21.9283 | 85.3797 | 0 | 5.24 | 6 | HAUL ROAD | 15.1674 | 2682
2024-12-18 | 20:28 | 21.9283 | 85.3797 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 2683
2024-12-18 | 20:28 | 21.9282 | 85.3797 | 3.16 | 23.79 | 6 | HAUL ROAD | 11.1192 | 2684
2024-12-18 | 20:28 | 21.9282 | 85.3798 | 18.36 | 36.16 | 6 | HAUL ROAD | 10.3152 | 2685
2024-12-18 | 20:28 | 21.9281 | 85.3798 | 71.53 | 55.2 | 6 | HAUL ROAD | 11.1192 | 2686
2024-12-18 | 20:28 | 21.9281 | 85.3798 | 156.12 | 3.16 | 6 | HAUL ROAD | 0 | 2687
2024-12-18 | 20:28 | 21.9281 | 85.3799 | 98.77 | 0 | 6 | HAUL ROAD | 10.3148 | 2688
2024-12-18 | 20:28 | 21.928 | 85.3799 | 52.48 | 0 | 6 | HAUL ROAD | 11.1192 | 2689
2024-12-18 | 20:28 | 21.928 | 85.3799 | 30.73 | 0 | 6 | HAUL ROAD | 0 | 2690
2024-12-18 | 20:28 | 21.928 | 85.38 | 10.12 | 0 | 6 | HAUL ROAD | 10.3152 | 2691
2024-12-18 | 20:28 | 21.9279 | 85.38 | 0 | 1.39 | 6 | HAUL ROAD | 11.1196 | 2692
2024-12-18 | 20:28 | 21.9279 | 85.38 | 3.16 | 1.39 | 6 | HAUL ROAD | 0 | 2693
2024-12-18 | 20:28 | 21.9278 | 85.38 | 3.16 | 7.58 | 6 | HAUL ROAD | 11.1192 | 2694
2024-12-18 | 20:28 | 21.9278 | 85.3799 | 3.16 | 5.24 | 6 | HAUL ROAD | 10.3148 | 2695
2024-12-18 | 20:28 | 21.9277 | 85.3799 | 3.16 | 3.16 | 6 | HAUL ROAD | 11.1196 | 2696
2024-12-18 | 20:28 | 21.9276 | 85.3798 | 7.58 | 1.39 | 6 | HAUL ROAD | 15.1674 | 2697
2024-12-18 | 20:28 | 21.9275 | 85.3797 | 12.8 | 5.24 | 6 | HAUL ROAD | 15.1674 | 2698
2024-12-18 | 20:28 | 21.9275 | 85.3797 | 21.12 | 1.39 | 6 | HAUL ROAD | 0.094935 | 2699
2024-12-18 | 20:28 | 21.9274 | 85.3796 | 26.31 | 10.12 | 6 | HAUL ROAD | 15.1674 | 2700
2024-12-18 | 20:28 | 21.9273 | 85.3796 | 44.32 | 0 | 6 | HAUL ROAD | 11.1196 | 2701
2024-12-18 | 20:28 | 21.9272 | 85.3796 | 5.24 | 5.24 | 6 | HAUL ROAD | 11.1196 | 2702
2024-12-18 | 20:28 | 21.9271 | 85.3795 | 30.73 | 7.58 | 6 | HAUL ROAD | 15.1674 | 2703
2024-12-18 | 20:29 | 21.9271 | 85.3795 | 12.8 | 12.8 | 6 | HAUL ROAD | 0.094935 | 2704
2024-12-18 | 20:29 | 21.927 | 85.3795 | 44.32 | 1.39 | 6 | HAUL ROAD | 11.12 | 2705
2024-12-18 | 20:29 | 21.9269 | 85.3795 | 21.12 | 10.12 | 6 | HAUL ROAD | 11.1192 | 2706
2024-12-18 | 20:29 | 21.9268 | 85.3795 | 23.79 | 0 | 6 | HAUL ROAD | 11.1196 | 2707
2024-12-18 | 20:29 | 21.9267 | 85.3794 | 7.58 | 0 | 6 | HAUL ROAD | 15.1674 | 2708
2024-12-18 | 20:29 | 21.9267 | 85.3794 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 2709
2024-12-18 | 20:29 | 21.9266 | 85.3794 | 1.39 | 0 | 6 | HAUL ROAD | 11.1192 | 2710
2024-12-18 | 20:29 | 21.9265 | 85.3794 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 2711
2024-12-18 | 20:29 | 21.9265 | 85.3794 | 1.39 | 0 | 6 | HAUL ROAD | 0.094935 | 2712
2024-12-18 | 20:29 | 21.9264 | 85.3794 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 2713
2024-12-18 | 20:29 | 21.9264 | 85.3794 | 0 | 0 | 6 | HAUL ROAD | 0 | 2714
2024-12-18 | 20:29 | 21.9263 | 85.3794 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 2715
2024-12-18 | 20:29 | 21.9263 | 85.3794 | 0 | 0 | 6 | HAUL ROAD | 0 | 2716
2024-12-18 | 20:29 | 21.9262 | 85.3794 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 2717
2024-12-18 | 20:29 | 21.9261 | 85.3794 | 0 | 1.39 | 6 | HAUL ROAD | 11.1196 | 2718
2024-12-18 | 20:29 | 21.926 | 85.3794 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 2719
2024-12-18 | 20:29 | 21.9259 | 85.3793 | 0 | 0 | 6 | HAUL ROAD | 15.1674 | 2720
2024-12-18 | 20:29 | 21.9258 | 85.3793 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 2721
2024-12-18 | 20:29 | 21.9256 | 85.3793 | 1.39 | 0 | 6 | HAUL ROAD | 22.239 | 2722
2024-12-18 | 20:29 | 21.9255 | 85.3793 | 1.39 | 1.39 | 6 | HAUL ROAD | 11.1192 | 2723
2024-12-18 | 20:29 | 21.9254 | 85.3792 | 10.12 | 0 | 6 | HAUL ROAD | 15.1671 | 2724
2024-12-18 | 20:29 | 21.9253 | 85.3792 | 0 | 1.39 | 6 | HAUL ROAD | 11.1196 | 2725
2024-12-18 | 20:29 | 21.9253 | 85.3791 | 3.16 | 12.8 | 6 | HAUL ROAD | 10.3152 | 2726
2024-12-18 | 20:29 | 21.9252 | 85.379 | 33.45 | 3.16 | 6 | HAUL ROAD | 15.1674 | 2727
2024-12-18 | 20:29 | 21.9251 | 85.379 | 15.57 | 3.16 | 6 | HAUL ROAD | 11.1196 | 2728
2024-12-18 | 20:29 | 21.925 | 85.3789 | 36.16 | 0 | 6 | HAUL ROAD | 15.1674 | 2729
2024-12-18 | 20:29 | 21.9249 | 85.3788 | 3.16 | 0 | 6 | HAUL ROAD | 15.1674 | 2730
2024-12-18 | 20:29 | 21.9249 | 85.3788 | 10.12 | 0 | 6 | HAUL ROAD | 0 | 2731
2024-12-18 | 20:29 | 21.9248 | 85.3787 | 0 | 0 | 6 | HAUL ROAD | 15.1674 | 2732
2024-12-18 | 20:29 | 21.9247 | 85.3787 | 3.16 | 0 | 6 | HAUL ROAD | 11.12 | 2733
2024-12-18 | 20:30 | 21.9247 | 85.3786 | 0 | 0 | 6 | HAUL ROAD | 10.3152 | 2734
2024-12-18 | 20:30 | 21.9246 | 85.3786 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 2735
2024-12-18 | 20:30 | 21.9245 | 85.3785 | 0 | 1.39 | 6 | HAUL ROAD | 15.1677 | 2736
2024-12-18 | 20:30 | 21.9245 | 85.3785 | 1.39 | 5.24 | 6 | HAUL ROAD | 0 | 2737
2024-12-18 | 20:30 | 21.9244 | 85.3784 | 0 | 5.24 | 6 | HAUL ROAD | 15.1671 | 2738
2024-12-18 | 20:30 | 21.9244 | 85.3784 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 2739
2024-12-18 | 20:30 | 21.9243 | 85.3783 | 1.39 | 5.24 | 6 | HAUL ROAD | 15.1674 | 2740
2024-12-18 | 20:30 | 21.9242 | 85.3783 | 1.39 | 7.58 | 6 | HAUL ROAD | 11.1192 | 2741
2024-12-18 | 20:30 | 21.9242 | 85.3783 | 0 | 0 | 6 | HAUL ROAD | 0 | 2742
2024-12-18 | 20:30 | 21.9242 | 85.3782 | 0 | 0 | 6 | HAUL ROAD | 10.3148 | 2743
2024-12-18 | 20:30 | 21.9242 | 85.3782 | 1.39 | 30.73 | 6 | HAUL ROAD | 0 | 2744
2024-12-18 | 20:30 | 21.9243 | 85.3782 | 7.58 | 26.31 | 6 | HAUL ROAD | 11.1192 | 2745
2024-12-18 | 20:30 | 21.9243 | 85.3782 | 5.24 | 0 | 6 | HAUL ROAD | 0.094935 | 2746
2024-12-18 | 20:30 | 21.9243 | 85.3782 | 3.16 | 0 | 6 | HAUL ROAD | 0.094935 | 2747
2024-12-18 | 20:30 | 21.9243 | 85.3782 | 5.24 | 0 | 6 | HAUL ROAD | 0.094935 | 2748
2024-12-18 | 20:30 | 21.9243 | 85.3782 | 3.16 | 0 | 6 | HAUL ROAD | 0.094935 | 2749
2024-12-18 | 20:30 | 21.9243 | 85.3782 | 5.24 | 0 | 6 | HAUL ROAD | 0.094935 | 2750
2024-12-18 | 20:30 | 21.9243 | 85.3782 | 5.24 | 0 | 6 | HAUL ROAD | 0.094935 | 2751
2024-12-18 | 20:30 | 21.9243 | 85.3782 | 5.24 | 0 | 6 | HAUL ROAD | 0.094935 | 2752
2024-12-18 | 20:30 | 21.9243 | 85.3782 | 5.24 | 0 | 6 | HAUL ROAD | 0.094935 | 2753
2024-12-18 | 20:30 | 21.9243 | 85.3782 | 5.24 | 0 | 6 | HAUL ROAD | 0.094935 | 2754
2024-12-18 | 20:30 | 21.9243 | 85.3782 | 5.24 | 0 | 6 | HAUL ROAD | 0.094935 | 2755
2024-12-18 | 20:30 | 21.9243 | 85.3782 | 1.39 | 0 | 6 | HAUL ROAD | 0.094935 | 2756
2024-12-18 | 20:31 | 21.9244 | 85.3779 | 142.45 | 68.8 | 15.1 | GARDEN SUBSTATION | 32.8831 | 2757
2024-12-18 | 20:31 | 21.9244 | 85.3779 | 384.51 | 260.34 | 15.1 | GARDEN SUBSTATION | 0 | 2758
2024-12-18 | 20:31 | 21.9244 | 85.3779 | 764.7 | 147.92 | 15.1 | GARDEN SUBSTATION | 0 | 2759
2024-12-18 | 20:31 | 21.9244 | 85.3779 | 683.01 | 66.08 | 15.1 | GARDEN SUBSTATION | 0 | 2760
2024-12-18 | 20:31 | 21.9244 | 85.3779 | 417.76 | 167.07 | 15.1 | GARDEN SUBSTATION | 0 | 2761
2024-12-18 | 20:31 | 21.9244 | 85.3779 | 459.4 | 230.12 | 15.1 | GARDEN SUBSTATION | 0 | 2762
2024-12-18 | 20:31 | 21.9244 | 85.3779 | 977.53 | 210.9 | 15.1 | GARDEN SUBSTATION | 0 | 2763
2024-12-18 | 20:31 | 21.9244 | 85.3779 | 1026.08 | 7.58 | 15.1 | GARDEN SUBSTATION | 0 | 2764
2024-12-18 | 20:31 | 21.9244 | 85.3779 | 484.43 | 52.48 | 15.1 | GARDEN SUBSTATION | 0 | 2765
2024-12-18 | 20:31 | 21.9244 | 85.3779 | 445.51 | 139.72 | 15.1 | GARDEN SUBSTATION | 0 | 2766
2024-12-18 | 20:31 | 21.9244 | 85.3779 | 903.49 | 21.12 | 15.1 | GARDEN SUBSTATION | 0 | 2767
2024-12-18 | 20:31 | 21.9244 | 85.3779 | 1026.08 | 79.7 | 15.1 | GARDEN SUBSTATION | 0 | 2768
2024-12-18 | 20:31 | 21.9244 | 85.3779 | 668.96 | 49.76 | 15.1 | GARDEN SUBSTATION | 0 | 2769
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 484.43 | 15.57 | 15.1 | GARDEN SUBSTATION | 0 | 2770
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 598.86 | 49.76 | 15.1 | GARDEN SUBSTATION | 0 | 2771
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 632.48 | 167.07 | 15.1 | GARDEN SUBSTATION | 0 | 2772
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 395.59 | 274.1 | 15.1 | GARDEN SUBSTATION | 0 | 2773
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 199.93 | 66.08 | 15.1 | GARDEN SUBSTATION | 0 | 2774
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 205.42 | 60.64 | 15.1 | GARDEN SUBSTATION | 0 | 2775
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 227.37 | 156.12 | 15.1 | GARDEN SUBSTATION | 0 | 2776
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 392.82 | 139.72 | 15.1 | GARDEN SUBSTATION | 0 | 2777
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 448.29 | 241.1 | 15.1 | GARDEN SUBSTATION | 0 | 2778
2024-12-18 | 20:32 | 21.9244 | 85.378 | 246.6 | 0 | 15.1 | GARDEN SUBSTATION | 10.3148 | 2779
2024-12-18 | 20:32 | 21.9243 | 85.378 | 23.79 | 1.39 | 6 | HAUL ROAD | 11.1196 | 2780
2024-12-18 | 20:32 | 21.9244 | 85.378 | 60.64 | 0 | 15.2 | FEEDER (GARDEN SUBSTATION) | 11.1196 | 2781
2024-12-18 | 20:32 | 21.9244 | 85.378 | 26.31 | 0 | 15.2 | FEEDER (GARDEN SUBSTATION) | 0 | 2782
2024-12-18 | 20:32 | 21.9244 | 85.378 | 23.79 | 3.16 | 15.2 | FEEDER (GARDEN SUBSTATION) | 0 | 2783
2024-12-18 | 20:32 | 21.9244 | 85.378 | 18.36 | 93.32 | 15.2 | FEEDER (GARDEN SUBSTATION) | 0 | 2784
2024-12-18 | 20:32 | 21.9244 | 85.378 | 38.88 | 44.32 | 15.2 | FEEDER (GARDEN SUBSTATION) | 0 | 2785
2024-12-18 | 20:32 | 21.9244 | 85.378 | 123.33 | 208.16 | 15.1 | GARDEN SUBSTATION | 0 | 2786
2024-12-18 | 20:32 | 21.9244 | 85.378 | 348.56 | 351.32 | 15.1 | GARDEN SUBSTATION | 0 | 2787
2024-12-18 | 20:32 | 21.9244 | 85.378 | 671.77 | 188.97 | 15.1 | GARDEN SUBSTATION | 0 | 2788
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 570.89 | 63.36 | 15.1 | GARDEN SUBSTATION | 10.3148 | 2789
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 172.54 | 104.23 | 15.1 | GARDEN SUBSTATION | 0 | 2790
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 387.28 | 145.18 | 15.1 | GARDEN SUBSTATION | 0 | 2791
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 390.05 | 60.64 | 15.1 | GARDEN SUBSTATION | 0 | 2792
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 362.38 | 18.36 | 15.1 | GARDEN SUBSTATION | 0 | 2793
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 156.12 | 439.96 | 15.1 | GARDEN SUBSTATION | 0 | 2794
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 120.6 | 431.63 | 15.1 | GARDEN SUBSTATION | 0 | 2795
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 126.06 | 437.18 | 15.1 | GARDEN SUBSTATION | 0 | 2796
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 150.65 | 414.99 | 15.1 | GARDEN SUBSTATION | 0 | 2797
2024-12-18 | 20:32 | 21.9244 | 85.3779 | 153.39 | 412.22 | 15.1 | GARDEN SUBSTATION | 0 | 2798
2024-12-18 | 20:34 | 21.9243 | 85.3782 | 3.16 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 32.8831 | 2799
2024-12-18 | 20:34 | 21.9243 | 85.3782 | 3.16 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0.094935 | 2800
2024-12-18 | 20:34 | 21.9243 | 85.3782 | 3.16 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0.094935 | 2801
2024-12-18 | 20:34 | 21.9243 | 85.3782 | 3.16 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0.094935 | 2802
2024-12-18 | 20:34 | 21.9243 | 85.3782 | 3.16 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0.094935 | 2803
2024-12-18 | 20:35 | 21.9243 | 85.3782 | 3.16 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0.094935 | 2804
2024-12-18 | 20:35 | 21.9243 | 85.3782 | 3.16 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0.094935 | 2805
2024-12-18 | 20:35 | 21.9243 | 85.3782 | 3.16 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0.094935 | 2806
2024-12-18 | 20:35 | 21.9243 | 85.3782 | 3.16 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0.094935 | 2807
2024-12-18 | 20:35 | 21.9243 | 85.3782 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0.094935 | 2808
2024-12-18 | 20:35 | 21.9243 | 85.3782 | 0 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0.094935 | 2809
2024-12-18 | 20:35 | 21.9243 | 85.3782 | 0 | 5.24 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0.094935 | 2810
2024-12-18 | 20:35 | 21.9243 | 85.3782 | 0 | 5.24 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0.094935 | 2811
2024-12-18 | 20:35 | 21.9243 | 85.3782 | 0 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0.094935 | 2812
2024-12-18 | 20:35 | 21.9243 | 85.3783 | 0 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3157 | 2813
2024-12-18 | 20:35 | 21.9243 | 85.3783 | 0 | 10.12 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0.094935 | 2814
2024-12-18 | 20:35 | 21.9242 | 85.3783 | 0 | 7.58 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2815
2024-12-18 | 20:35 | 21.9242 | 85.3782 | 1.39 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3148 | 2816
2024-12-18 | 20:35 | 21.9241 | 85.3782 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2817
2024-12-18 | 20:35 | 21.9241 | 85.3781 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3152 | 2818
2024-12-18 | 20:35 | 21.924 | 85.3781 | 0 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2819
2024-12-18 | 20:35 | 21.924 | 85.3781 | 0 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2820
2024-12-18 | 20:35 | 21.924 | 85.3781 | 0 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2821
2024-12-18 | 20:35 | 21.924 | 85.3781 | 0 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2822
2024-12-18 | 20:35 | 21.924 | 85.3781 | 0 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2823
2024-12-18 | 20:35 | 21.924 | 85.3781 | 0 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2824
2024-12-18 | 20:35 | 21.924 | 85.3781 | 0 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2825
2024-12-18 | 20:35 | 21.924 | 85.3781 | 0 | 5.24 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2826
2024-12-18 | 20:35 | 21.9239 | 85.3781 | 0 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2827
2024-12-18 | 20:35 | 21.9239 | 85.3781 | 0 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2828
2024-12-18 | 20:35 | 21.9238 | 85.3781 | 0 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2829
2024-12-18 | 20:35 | 21.9237 | 85.378 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1671 | 2830
2024-12-18 | 20:35 | 21.9237 | 85.378 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2831
2024-12-18 | 20:35 | 21.9236 | 85.378 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2832
2024-12-18 | 20:35 | 21.9235 | 85.3779 | 0 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1674 | 2833
2024-12-18 | 20:36 | 21.9234 | 85.3779 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2834
2024-12-18 | 20:36 | 21.9233 | 85.3779 | 0 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2835
2024-12-18 | 20:36 | 21.9233 | 85.3778 | 3.16 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3157 | 2836
2024-12-18 | 20:36 | 21.9232 | 85.3778 | 3.16 | 5.24 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2837
2024-12-18 | 20:36 | 21.9231 | 85.3777 | 7.58 | 5.24 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2838
2024-12-18 | 20:36 | 21.923 | 85.3777 | 7.58 | 7.58 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2839
2024-12-18 | 20:36 | 21.9229 | 85.3776 | 7.58 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2840
2024-12-18 | 20:36 | 21.9229 | 85.3775 | 5.24 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3157 | 2841
2024-12-18 | 20:36 | 21.9228 | 85.3775 | 1.39 | 5.24 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2842
2024-12-18 | 20:36 | 21.9227 | 85.3774 | 1.39 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2843
2024-12-18 | 20:36 | 21.9227 | 85.3774 | 1.39 | 5.24 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2844
2024-12-18 | 20:36 | 21.9226 | 85.3774 | 1.39 | 7.58 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2845
2024-12-18 | 20:36 | 21.9226 | 85.3774 | 1.39 | 5.24 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2846
2024-12-18 | 20:36 | 21.9225 | 85.3773 | 5.24 | 5.24 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2847
2024-12-18 | 20:36 | 21.9224 | 85.3773 | 3.16 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2848
2024-12-18 | 20:36 | 21.9223 | 85.3772 | 5.24 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2849
2024-12-18 | 20:36 | 21.9223 | 85.3771 | 3.16 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3157 | 2850
2024-12-18 | 20:36 | 21.9222 | 85.3771 | 1.39 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.12 | 2851
2024-12-18 | 20:36 | 21.9221 | 85.3771 | 5.24 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2852
2024-12-18 | 20:36 | 21.922 | 85.377 | 5.24 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2853
2024-12-18 | 20:36 | 21.9219 | 85.377 | 21.12 | 7.58 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.12 | 2854
2024-12-18 | 20:36 | 21.9218 | 85.377 | 23.79 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2855
2024-12-18 | 20:36 | 21.9218 | 85.377 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2856
2024-12-18 | 20:36 | 21.9217 | 85.377 | 0 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2857
2024-12-18 | 20:36 | 21.9216 | 85.377 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2858
2024-12-18 | 20:36 | 21.9215 | 85.377 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.12 | 2859
2024-12-18 | 20:36 | 21.9214 | 85.3771 | 12.8 | 18.36 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2860
2024-12-18 | 20:36 | 21.9213 | 85.3772 | 76.97 | 5.24 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2861
2024-12-18 | 20:36 | 21.9212 | 85.3772 | 60.64 | 15.57 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2862
2024-12-18 | 20:36 | 21.9212 | 85.3773 | 23.79 | 5.24 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3161 | 2863
2024-12-18 | 20:37 | 21.9211 | 85.3773 | 55.2 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2864
2024-12-18 | 20:37 | 21.921 | 85.3774 | 23.79 | 12.8 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2865
2024-12-18 | 20:37 | 21.9209 | 85.3773 | 47.04 | 7.58 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2866
2024-12-18 | 20:37 | 21.9208 | 85.3773 | 60.64 | 7.58 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2867
2024-12-18 | 20:37 | 21.9207 | 85.3773 | 36.16 | 23.79 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2868
2024-12-18 | 20:37 | 21.9207 | 85.3772 | 57.92 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3152 | 2869
2024-12-18 | 20:37 | 21.9206 | 85.3772 | 26.31 | 12.8 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2870
2024-12-18 | 20:37 | 21.9205 | 85.3771 | 71.53 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1674 | 2871
2024-12-18 | 20:37 | 21.9204 | 85.3771 | 23.79 | 12.8 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2872
2024-12-18 | 20:37 | 21.9204 | 85.377 | 60.64 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3152 | 2873
2024-12-18 | 20:37 | 21.9203 | 85.377 | 21.12 | 10.12 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2874
2024-12-18 | 20:37 | 21.9202 | 85.3769 | 26.31 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2875
2024-12-18 | 20:37 | 21.9201 | 85.3768 | 7.58 | 10.12 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2876
2024-12-18 | 20:37 | 21.9201 | 85.3768 | 1.39 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2877
2024-12-18 | 20:37 | 21.92 | 85.3767 | 3.16 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2878
2024-12-18 | 20:37 | 21.92 | 85.3766 | 10.12 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3157 | 2879
2024-12-18 | 20:37 | 21.92 | 85.3765 | 3.16 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3157 | 2880
2024-12-18 | 20:37 | 21.92 | 85.3764 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3157 | 2881
2024-12-18 | 20:37 | 21.9201 | 85.3763 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2882
2024-12-18 | 20:37 | 21.9201 | 85.3762 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3157 | 2883
2024-12-18 | 20:37 | 21.9202 | 85.3762 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2884
2024-12-18 | 20:37 | 21.9202 | 85.3761 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3152 | 2885
2024-12-18 | 20:37 | 21.9203 | 85.376 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2886
2024-12-18 | 20:37 | 21.9203 | 85.3759 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3157 | 2887
2024-12-18 | 20:37 | 21.9203 | 85.3758 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3157 | 2888
2024-12-18 | 20:37 | 21.9202 | 85.3757 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2889
2024-12-18 | 20:37 | 21.9202 | 85.3756 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3152 | 2890
2024-12-18 | 20:37 | 21.9202 | 85.3755 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3152 | 2891
2024-12-18 | 20:37 | 21.9201 | 85.3754 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2892
2024-12-18 | 20:37 | 21.92 | 85.3753 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2893
2024-12-18 | 20:38 | 21.92 | 85.3752 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3157 | 2894
2024-12-18 | 20:38 | 21.9199 | 85.3752 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2895
2024-12-18 | 20:38 | 21.9198 | 85.3751 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2896
2024-12-18 | 20:38 | 21.9197 | 85.375 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2897
2024-12-18 | 20:38 | 21.9196 | 85.3749 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2898
2024-12-18 | 20:38 | 21.9195 | 85.3748 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2899
2024-12-18 | 20:38 | 21.9195 | 85.3748 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2900
2024-12-18 | 20:38 | 21.9194 | 85.3747 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2901
2024-12-18 | 20:38 | 21.9193 | 85.3746 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2902
2024-12-18 | 20:38 | 21.9192 | 85.3746 | 0 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2903
2024-12-18 | 20:38 | 21.9191 | 85.3745 | 5.24 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2904
2024-12-18 | 20:38 | 21.919 | 85.3744 | 7.58 | 5.24 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2905
2024-12-18 | 20:38 | 21.9189 | 85.3744 | 3.16 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2906
2024-12-18 | 20:38 | 21.9188 | 85.3743 | 3.16 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1674 | 2907
2024-12-18 | 20:38 | 21.9187 | 85.3743 | 5.24 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2908
2024-12-18 | 20:38 | 21.9186 | 85.3742 | 3.16 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.168 | 2909
2024-12-18 | 20:38 | 21.9185 | 85.3742 | 7.58 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.12 | 2910
2024-12-18 | 20:38 | 21.9184 | 85.3741 | 5.24 | 5.24 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2911
2024-12-18 | 20:38 | 21.9184 | 85.3741 | 10.12 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2912
2024-12-18 | 20:38 | 21.9183 | 85.374 | 12.8 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2913
2024-12-18 | 20:38 | 21.9182 | 85.374 | 7.58 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2914
2024-12-18 | 20:38 | 21.9181 | 85.374 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2915
2024-12-18 | 20:38 | 21.9181 | 85.374 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2916
2024-12-18 | 20:38 | 21.918 | 85.374 | 0 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2917
2024-12-18 | 20:38 | 21.918 | 85.374 | 0 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2918
2024-12-18 | 20:38 | 21.918 | 85.3741 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3157 | 2919
2024-12-18 | 20:38 | 21.918 | 85.3741 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2920
2024-12-18 | 20:38 | 21.9181 | 85.3741 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2921
2024-12-18 | 20:38 | 21.9182 | 85.3742 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2922
2024-12-18 | 20:38 | 21.9182 | 85.3742 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 0 | 2923
2024-12-18 | 20:39 | 21.9183 | 85.3743 | 0 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2924
2024-12-18 | 20:39 | 21.9184 | 85.3743 | 0 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2925
2024-12-18 | 20:39 | 21.9185 | 85.3744 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2926
2024-12-18 | 20:39 | 21.9185 | 85.3745 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3157 | 2927
2024-12-18 | 20:39 | 21.9186 | 85.3745 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.12 | 2928
2024-12-18 | 20:39 | 21.9187 | 85.3746 | 0 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.168 | 2929
2024-12-18 | 20:39 | 21.9188 | 85.3746 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2930
2024-12-18 | 20:39 | 21.9188 | 85.3747 | 0 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3152 | 2931
2024-12-18 | 20:39 | 21.9189 | 85.3747 | 0 | 1.39 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2932
2024-12-18 | 20:39 | 21.9189 | 85.3748 | 0 | 3.16 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3157 | 2933
2024-12-18 | 20:39 | 21.919 | 85.3749 | 0 | 10.12 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 15.1677 | 2934
2024-12-18 | 20:39 | 21.9191 | 85.3749 | 0 | 12.8 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1192 | 2935
2024-12-18 | 20:39 | 21.9191 | 85.375 | 0 | 10.12 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3161 | 2936
2024-12-18 | 20:39 | 21.9192 | 85.375 | 3.16 | 7.58 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 11.1196 | 2937
2024-12-18 | 20:39 | 21.9192 | 85.3751 | 0 | 0 | 6 | HAUL ROAD (GARDEN S/S TO PIT-3 QUARRY) | 10.3157 | 2938
2024-12-18 | 20:39 | 21.9193 | 85.3751 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 2939
2024-12-18 | 20:39 | 21.9193 | 85.3752 | 0 | 0 | 6 | HAUL ROAD | 10.3157 | 2940
2024-12-18 | 20:39 | 21.9192 | 85.3752 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 2941
2024-12-18 | 20:39 | 21.9192 | 85.3752 | 21.12 | 106.96 | 6 | HAUL ROAD | 0 | 2942
2024-12-18 | 20:39 | 21.9191 | 85.3751 | 47.04 | 131.52 | 6 | HAUL ROAD | 15.1677 | 2943
2024-12-18 | 20:39 | 21.9191 | 85.3751 | 98.77 | 0 | 6 | HAUL ROAD | 0.094935 | 2944
2024-12-18 | 20:39 | 21.9191 | 85.375 | 15.57 | 1.39 | 6 | HAUL ROAD | 10.3161 | 2945
2024-12-18 | 20:39 | 21.919 | 85.3749 | 0 | 1.39 | 6 | HAUL ROAD | 15.1677 | 2946
2024-12-18 | 20:39 | 21.919 | 85.3749 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 2947
2024-12-18 | 20:39 | 21.9189 | 85.3748 | 0 | 0 | 6 | HAUL ROAD | 15.1677 | 2948
2024-12-18 | 20:39 | 21.9189 | 85.3747 | 0 | 0 | 6 | HAUL ROAD | 10.3157 | 2949
2024-12-18 | 20:39 | 21.9188 | 85.3747 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 2950
2024-12-18 | 20:39 | 21.9187 | 85.3746 | 0 | 1.39 | 6 | HAUL ROAD | 15.1677 | 2951
2024-12-18 | 20:39 | 21.9187 | 85.3746 | 0 | 1.39 | 6 | HAUL ROAD | 0.094935 | 2952
2024-12-18 | 20:39 | 21.9186 | 85.3745 | 0 | 0 | 6 | HAUL ROAD | 15.168 | 2953
2024-12-18 | 20:40 | 21.9186 | 85.3745 | 0 | 0 | 6 | HAUL ROAD | 0 | 2954
2024-12-18 | 20:40 | 21.9185 | 85.3744 | 0 | 0 | 6 | HAUL ROAD | 15.1677 | 2955
2024-12-18 | 20:40 | 21.9184 | 85.3744 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 2956
2024-12-18 | 20:40 | 21.9184 | 85.3743 | 0 | 0 | 6 | HAUL ROAD | 10.3157 | 2957
2024-12-18 | 20:40 | 21.9183 | 85.3743 | 0 | 3.16 | 6 | HAUL ROAD | 11.1196 | 2958
2024-12-18 | 20:40 | 21.9183 | 85.3743 | 1.39 | 0 | 6 | HAUL ROAD | 0 | 2959
2024-12-18 | 20:40 | 21.9182 | 85.3742 | 0 | 0 | 6 | HAUL ROAD | 15.1677 | 2960
2024-12-18 | 20:40 | 21.9182 | 85.3742 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 2961
2024-12-18 | 20:40 | 21.9181 | 85.3741 | 0 | 0 | 6 | HAUL ROAD | 15.1677 | 2962
2024-12-18 | 20:40 | 21.9181 | 85.3741 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 2963
2024-12-18 | 20:40 | 21.918 | 85.3741 | 3.16 | 1.39 | 6 | HAUL ROAD | 11.1192 | 2964
2024-12-18 | 20:40 | 21.918 | 85.374 | 1.39 | 1.39 | 6 | HAUL ROAD | 10.3157 | 2965
2024-12-18 | 20:40 | 21.918 | 85.374 | 3.16 | 5.24 | 6 | HAUL ROAD | 0 | 2966
2024-12-18 | 20:40 | 21.918 | 85.374 | 1.39 | 3.16 | 6 | HAUL ROAD | 0 | 2967
2024-12-18 | 20:40 | 21.918 | 85.374 | 0 | 0 | 6 | HAUL ROAD | 0 | 2968
2024-12-18 | 20:40 | 21.918 | 85.374 | 0 | 0 | 6 | HAUL ROAD | 0 | 2969
2024-12-18 | 20:40 | 21.918 | 85.374 | 0 | 0 | 6 | HAUL ROAD | 0 | 2970
2024-12-18 | 20:40 | 21.918 | 85.374 | 1.39 | 3.16 | 6 | HAUL ROAD | 0 | 2971
2024-12-18 | 20:40 | 21.918 | 85.374 | 1.39 | 0 | 6 | HAUL ROAD | 0 | 2972
2024-12-18 | 20:40 | 21.9181 | 85.374 | 1.39 | 3.16 | 6 | HAUL ROAD | 11.1192 | 2973
2024-12-18 | 20:40 | 21.9182 | 85.374 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 2974
2024-12-18 | 20:40 | 21.9182 | 85.374 | 10.12 | 0 | 6 | HAUL ROAD | 0 | 2975
2024-12-18 | 20:40 | 21.9183 | 85.3741 | 10.12 | 1.39 | 6 | HAUL ROAD | 15.1677 | 2976
2024-12-18 | 20:40 | 21.9184 | 85.3741 | 10.12 | 1.39 | 6 | HAUL ROAD | 11.1196 | 2977
2024-12-18 | 20:40 | 21.9185 | 85.3741 | 15.57 | 0 | 6 | HAUL ROAD | 11.1196 | 2978
2024-12-18 | 20:40 | 21.9186 | 85.3741 | 7.58 | 0 | 6 | HAUL ROAD | 11.12 | 2979
2024-12-18 | 20:40 | 21.9187 | 85.3742 | 3.16 | 0 | 6 | HAUL ROAD | 15.168 | 2980
2024-12-18 | 20:40 | 21.9188 | 85.3743 | 10.12 | 1.39 | 6 | HAUL ROAD | 15.1677 | 2981
2024-12-18 | 20:40 | 21.9189 | 85.3743 | 7.58 | 1.39 | 6 | HAUL ROAD | 11.1192 | 2982
2024-12-18 | 20:40 | 21.919 | 85.3744 | 7.58 | 0 | 6 | HAUL ROAD | 15.1677 | 2983
2024-12-18 | 20:41 | 21.9191 | 85.3744 | 7.58 | 3.16 | 6 | HAUL ROAD | 11.1192 | 2984
2024-12-18 | 20:41 | 21.9192 | 85.3745 | 12.8 | 0 | 6 | HAUL ROAD | 15.1677 | 2985
2024-12-18 | 20:41 | 21.9192 | 85.3746 | 10.12 | 0 | 6 | HAUL ROAD | 10.3157 | 2986
2024-12-18 | 20:41 | 21.9193 | 85.3746 | 3.16 | 0 | 6 | HAUL ROAD | 11.1196 | 2987
2024-12-18 | 20:41 | 21.9194 | 85.3747 | 0 | 0 | 6 | HAUL ROAD | 15.1677 | 2988
2024-12-18 | 20:41 | 21.9194 | 85.3748 | 0 | 0 | 6 | HAUL ROAD | 10.3161 | 2989
2024-12-18 | 20:41 | 21.9195 | 85.3748 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 2990
2024-12-18 | 20:41 | 21.9196 | 85.3749 | 0 | 0 | 6 | HAUL ROAD | 15.1677 | 2991
2024-12-18 | 20:41 | 21.9197 | 85.375 | 0 | 0 | 6 | HAUL ROAD | 15.1677 | 2992
2024-12-18 | 20:41 | 21.9198 | 85.3751 | 0 | 0 | 6 | HAUL ROAD | 15.1677 | 2993
2024-12-18 | 20:41 | 21.9199 | 85.3751 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 2994
2024-12-18 | 20:41 | 21.92 | 85.3752 | 0 | 0 | 6 | HAUL ROAD | 15.1677 | 2995
2024-12-18 | 20:41 | 21.92 | 85.3753 | 0 | 0 | 6 | HAUL ROAD | 10.3157 | 2996
2024-12-18 | 20:41 | 21.9201 | 85.3754 | 0 | 0 | 6 | HAUL ROAD | 15.1677 | 2997
2024-12-18 | 20:41 | 21.9202 | 85.3755 | 0 | 0 | 6 | HAUL ROAD | 15.1677 | 2998
2024-12-18 | 20:41 | 21.9202 | 85.3756 | 0 | 0 | 6 | HAUL ROAD | 10.3152 | 2999
2024-12-18 | 20:41 | 21.9203 | 85.3757 | 0 | 0 | 6 | HAUL ROAD | 15.1677 | 3000
2024-12-18 | 20:41 | 21.9203 | 85.3758 | 0 | 0 | 6 | HAUL ROAD | 10.3157 | 3001
2024-12-18 | 20:41 | 21.9203 | 85.3759 | 0 | 0 | 6 | HAUL ROAD | 10.3157 | 3002
2024-12-18 | 20:41 | 21.9203 | 85.376 | 0 | 0 | 6 | HAUL ROAD | 10.3157 | 3003
2024-12-18 | 20:41 | 21.9203 | 85.3761 | 0 | 0 | 6 | HAUL ROAD | 10.3157 | 3004
2024-12-18 | 20:41 | 21.9202 | 85.3762 | 0 | 0 | 6 | HAUL ROAD | 15.1677 | 3005
2024-12-18 | 20:41 | 21.9201 | 85.3763 | 0 | 0 | 6 | HAUL ROAD | 15.1677 | 3006
2024-12-18 | 20:41 | 21.9201 | 85.3764 | 0 | 0 | 6 | HAUL ROAD | 10.3157 | 3007
2024-12-18 | 20:41 | 21.9201 | 85.3765 | 1.39 | 0 | 6 | HAUL ROAD | 10.3157 | 3008
2024-12-18 | 20:41 | 21.9201 | 85.3766 | 15.57 | 7.58 | 6 | HAUL ROAD | 10.3157 | 3009
2024-12-18 | 20:41 | 21.9201 | 85.3766 | 63.36 | 12.8 | 6 | HAUL ROAD | 0 | 3010
2024-12-18 | 20:41 | 21.9201 | 85.3767 | 131.52 | 10.12 | 6 | HAUL ROAD | 10.3157 | 3011
2024-12-18 | 20:41 | 21.9202 | 85.3768 | 79.7 | 15.57 | 6 | HAUL ROAD | 15.1677 | 3012
2024-12-18 | 20:41 | 21.9202 | 85.3769 | 66.08 | 15.57 | 6 | HAUL ROAD | 10.3152 | 3013
2024-12-18 | 20:42 | 21.9203 | 85.377 | 55.2 | 26.31 | 6 | HAUL ROAD | 15.1677 | 3014
2024-12-18 | 20:42 | 21.9204 | 85.377 | 74.25 | 30.73 | 6 | HAUL ROAD | 11.1192 | 3015
2024-12-18 | 20:42 | 21.9205 | 85.3771 | 126.06 | 30.73 | 6 | HAUL ROAD | 15.1674 | 3016
2024-12-18 | 20:42 | 21.9206 | 85.3771 | 68.8 | 36.16 | 6 | HAUL ROAD | 11.1192 | 3017
2024-12-18 | 20:42 | 21.9207 | 85.3772 | 142.45 | 21.12 | 6 | HAUL ROAD | 15.1674 | 3018
2024-12-18 | 20:42 | 21.9208 | 85.3773 | 55.2 | 18.36 | 6 | HAUL ROAD | 15.1677 | 3019
2024-12-18 | 20:42 | 21.9208 | 85.3773 | 63.36 | 15.57 | 6 | HAUL ROAD | 0 | 3020
2024-12-18 | 20:42 | 21.9209 | 85.3774 | 30.73 | 1.39 | 6 | HAUL ROAD | 15.1677 | 3021
2024-12-18 | 20:42 | 21.9209 | 85.3774 | 12.8 | 0 | 6 | HAUL ROAD | 0 | 3022
2024-12-18 | 20:42 | 21.921 | 85.3775 | 1.39 | 0 | 6 | HAUL ROAD | 15.1677 | 3023
2024-12-18 | 20:42 | 21.921 | 85.3775 | 3.16 | 0 | 6 | HAUL ROAD | 0 | 3024
2024-12-18 | 20:42 | 21.9211 | 85.3776 | 1.39 | 0 | 6 | HAUL ROAD | 15.1677 | 3025
2024-12-18 | 20:42 | 21.9211 | 85.3776 | 0 | 0 | 6 | HAUL ROAD | 0 | 3026
2024-12-18 | 20:42 | 21.9212 | 85.3776 | 5.24 | 3.16 | 6 | HAUL ROAD | 11.1196 | 3027
2024-12-18 | 20:42 | 21.9213 | 85.3776 | 44.32 | 5.24 | 6 | HAUL ROAD | 11.1192 | 3028
2024-12-18 | 20:42 | 21.9214 | 85.3776 | 66.08 | 3.16 | 4 | S10 STOCK | 11.1196 | 3029
2024-12-18 | 20:42 | 21.9214 | 85.3777 | 33.45 | 5.24 | 4 | S10 STOCK | 10.3161 | 3030
2024-12-18 | 20:42 | 21.9215 | 85.3777 | 36.16 | 3.16 | 4 | S10 STOCK | 11.1196 | 3031
2024-12-18 | 20:42 | 21.9215 | 85.3777 | 44.32 | 3.16 | 4 | S10 STOCK | 0 | 3032
2024-12-18 | 20:42 | 21.9216 | 85.3777 | 26.31 | 3.16 | 4 | S10 STOCK | 11.12 | 3033
2024-12-18 | 20:42 | 21.9216 | 85.3778 | 21.12 | 5.24 | 4 | S10 STOCK | 10.3157 | 3034
2024-12-18 | 20:42 | 21.9217 | 85.3778 | 23.79 | 10.12 | 4 | S10 STOCK | 11.1196 | 3035
2024-12-18 | 20:42 | 21.9217 | 85.3778 | 33.45 | 0 | 4 | S10 STOCK | 0.094935 | 3036
2024-12-18 | 20:42 | 21.9218 | 85.3779 | 26.31 | 0 | 6 | HAUL ROAD | 15.1677 | 3037
2024-12-18 | 20:42 | 21.9218 | 85.3779 | 12.8 | 0 | 6 | HAUL ROAD | 0 | 3038
2024-12-18 | 20:42 | 21.9218 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 3039
2024-12-18 | 20:42 | 21.9218 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 3040
2024-12-18 | 20:42 | 21.9218 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 3041
2024-12-18 | 20:42 | 21.9218 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 3042
2024-12-18 | 20:42 | 21.9218 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 3043
2024-12-18 | 20:43 | 21.9218 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 3044
2024-12-18 | 20:43 | 21.9218 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 3045
2024-12-18 | 20:43 | 21.9218 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 3046
2024-12-18 | 20:43 | 21.9218 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 3047
2024-12-18 | 20:43 | 21.9218 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 3048
2024-12-18 | 20:43 | 21.9218 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 3049
2024-12-18 | 20:43 | 21.9218 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 3050
2024-12-18 | 20:43 | 21.9218 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 3051
2024-12-18 | 20:43 | 21.9218 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 3052
2024-12-18 | 20:43 | 21.9218 | 85.3779 | 5.24 | 0 | 6 | HAUL ROAD | 0 | 3053
2024-12-18 | 20:43 | 21.9219 | 85.3779 | 1.39 | 0 | 6 | HAUL ROAD | 11.1196 | 3054
2024-12-18 | 20:43 | 21.9219 | 85.378 | 0 | 1.39 | 6 | HAUL ROAD | 10.3157 | 3055
2024-12-18 | 20:43 | 21.922 | 85.378 | 0 | 3.16 | 6 | HAUL ROAD | 11.12 | 3056
2024-12-18 | 20:43 | 21.922 | 85.378 | 0 | 3.16 | 6 | HAUL ROAD | 0.094935 | 3057
2024-12-18 | 20:43 | 21.9221 | 85.3781 | 10.12 | 12.8 | 6 | HAUL ROAD | 15.1677 | 3058
2024-12-18 | 20:43 | 21.9221 | 85.3781 | 44.32 | 10.12 | 6 | HAUL ROAD | 0 | 3059
2024-12-18 | 20:43 | 21.9222 | 85.3782 | 57.92 | 1.39 | 6 | HAUL ROAD | 15.1677 | 3060
2024-12-18 | 20:43 | 21.9222 | 85.3782 | 26.31 | 5.24 | 6 | HAUL ROAD | 0.094935 | 3061
2024-12-18 | 20:43 | 21.9223 | 85.3782 | 23.79 | 10.12 | 6 | HAUL ROAD | 11.12 | 3062
2024-12-18 | 20:43 | 21.9223 | 85.3783 | 36.16 | 3.16 | 6 | HAUL ROAD | 10.3157 | 3063
2024-12-18 | 20:43 | 21.9224 | 85.3783 | 30.73 | 3.16 | 6 | HAUL ROAD | 11.1196 | 3064
2024-12-18 | 20:43 | 21.9225 | 85.3783 | 23.79 | 7.58 | 6 | HAUL ROAD | 11.1196 | 3065
2024-12-18 | 20:43 | 21.9225 | 85.3783 | 38.88 | 3.16 | 6 | HAUL ROAD | 0 | 3066
2024-12-18 | 20:43 | 21.9226 | 85.3784 | 33.45 | 3.16 | 6 | HAUL ROAD | 15.1677 | 3067
2024-12-18 | 20:43 | 21.9227 | 85.3784 | 30.73 | 12.8 | 6 | HAUL ROAD | 11.1192 | 3068
2024-12-18 | 20:43 | 21.9227 | 85.3785 | 68.8 | 7.58 | 6 | HAUL ROAD | 10.3152 | 3069
2024-12-18 | 20:43 | 21.9228 | 85.3785 | 52.48 | 7.58 | 6 | HAUL ROAD | 11.1192 | 3070
2024-12-18 | 20:43 | 21.9229 | 85.3786 | 52.48 | 12.8 | 6 | HAUL ROAD | 15.1677 | 3071
2024-12-18 | 20:43 | 21.923 | 85.3787 | 44.32 | 7.58 | 6 | HAUL ROAD | 15.1677 | 3072
2024-12-18 | 20:43 | 21.9231 | 85.3787 | 21.12 | 15.57 | 6 | HAUL ROAD | 11.1196 | 3073
2024-12-18 | 20:44 | 21.9232 | 85.3787 | 26.31 | 12.8 | 6 | HAUL ROAD | 11.1192 | 3074
2024-12-18 | 20:44 | 21.9233 | 85.3788 | 18.36 | 15.57 | 6 | HAUL ROAD | 15.1674 | 3075
2024-12-18 | 20:44 | 21.9234 | 85.3788 | 12.8 | 21.12 | 6 | HAUL ROAD | 11.1196 | 3076
2024-12-18 | 20:44 | 21.9234 | 85.3788 | 12.8 | 18.36 | 6 | HAUL ROAD | 0 | 3077
2024-12-18 | 20:44 | 21.9235 | 85.3788 | 1.39 | 12.8 | 6 | HAUL ROAD | 11.1192 | 3078
2024-12-18 | 20:44 | 21.9236 | 85.3787 | 12.8 | 33.45 | 6 | HAUL ROAD | 15.1674 | 3079
2024-12-18 | 20:44 | 21.9237 | 85.3786 | 21.12 | 1.39 | 6 | HAUL ROAD | 15.1671 | 3080
2024-12-18 | 20:44 | 21.9237 | 85.3786 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 3081
2024-12-18 | 20:44 | 21.9237 | 85.3785 | 1.39 | 3.16 | 6 | HAUL ROAD | 10.3152 | 3082
2024-12-18 | 20:44 | 21.9238 | 85.3785 | 1.39 | 5.24 | 6 | HAUL ROAD | 11.1192 | 3083
2024-12-18 | 20:44 | 21.9238 | 85.3784 | 0 | 1.39 | 6 | HAUL ROAD | 10.3148 | 3084
2024-12-18 | 20:44 | 21.9239 | 85.3784 | 0 | 1.39 | 6 | HAUL ROAD | 11.1192 | 3085
2024-12-18 | 20:44 | 21.924 | 85.3784 | 0 | 3.16 | 6 | HAUL ROAD | 11.1196 | 3086
2024-12-18 | 20:44 | 21.924 | 85.3785 | 0 | 7.58 | 6 | HAUL ROAD | 10.3148 | 3087
2024-12-18 | 20:44 | 21.924 | 85.3785 | 0 | 0 | 6 | HAUL ROAD | 0 | 3088
2024-12-18 | 20:44 | 21.924 | 85.3786 | 0 | 0 | 6 | HAUL ROAD | 10.3148 | 3089
2024-12-18 | 20:44 | 21.9239 | 85.3786 | 0 | 3.16 | 6 | HAUL ROAD | 11.1196 | 3090
2024-12-18 | 20:44 | 21.9239 | 85.3787 | 0 | 1.39 | 6 | HAUL ROAD | 10.3152 | 3091
2024-12-18 | 20:44 | 21.9239 | 85.3788 | 0 | 3.16 | 6 | HAUL ROAD | 10.3152 | 3092
2024-12-18 | 20:44 | 21.9239 | 85.3789 | 3.16 | 10.12 | 4 | S11 STOCK | 10.3152 | 3093
2024-12-18 | 20:44 | 21.9239 | 85.3789 | 12.8 | 21.12 | 4 | S11 STOCK | 0 | 3094
2024-12-18 | 20:44 | 21.9239 | 85.379 | 30.73 | 10.12 | 4 | S11 STOCK | 10.3152 | 3095
2024-12-18 | 20:44 | 21.9239 | 85.3791 | 18.36 | 10.12 | 4 | S11 STOCK | 10.3152 | 3096
2024-12-18 | 20:44 | 21.924 | 85.3792 | 15.57 | 15.57 | 4 | S11 STOCK | 15.1674 | 3097
2024-12-18 | 20:44 | 21.9241 | 85.3792 | 52.48 | 12.8 | 4 | S11 STOCK | 11.1192 | 3098
2024-12-18 | 20:44 | 21.9241 | 85.3793 | 36.16 | 3.16 | 4 | S11 STOCK | 10.3152 | 3099
2024-12-18 | 20:44 | 21.9242 | 85.3792 | 12.8 | 3.16 | 6 | HAUL ROAD | 15.1671 | 3100
2024-12-18 | 20:44 | 21.9242 | 85.3792 | 0 | 7.58 | 6 | HAUL ROAD | 0 | 3101
2024-12-18 | 20:44 | 21.9242 | 85.3791 | 1.39 | 0 | 6 | HAUL ROAD | 10.3148 | 3102
2024-12-18 | 20:44 | 21.9241 | 85.379 | 0 | 1.39 | 6 | HAUL ROAD | 15.1671 | 3103
2024-12-18 | 20:45 | 21.9241 | 85.379 | 1.39 | 7.58 | 6 | HAUL ROAD | 0 | 3104
2024-12-18 | 20:45 | 21.924 | 85.3789 | 0 | 3.16 | 6 | HAUL ROAD | 15.1671 | 3105
2024-12-18 | 20:45 | 21.924 | 85.3788 | 0 | 0 | 6 | HAUL ROAD | 10.3148 | 3106
2024-12-18 | 20:45 | 21.9239 | 85.3787 | 0 | 0 | 6 | HAUL ROAD | 15.1674 | 3107
2024-12-18 | 20:45 | 21.9239 | 85.3786 | 0 | 0 | 6 | HAUL ROAD | 10.3152 | 3108
2024-12-18 | 20:45 | 21.924 | 85.3786 | 0 | 3.16 | 6 | HAUL ROAD | 11.1196 | 3109
2024-12-18 | 20:45 | 21.924 | 85.3785 | 0 | 7.58 | 6 | HAUL ROAD | 10.3148 | 3110
2024-12-18 | 20:45 | 21.924 | 85.3785 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 3111
2024-12-18 | 20:45 | 21.924 | 85.3784 | 3.16 | 12.8 | 6 | HAUL ROAD | 10.3148 | 3112
2024-12-18 | 20:45 | 21.924 | 85.3783 | 1.39 | 0 | 6 | HAUL ROAD | 10.3148 | 3113
2024-12-18 | 20:45 | 21.924 | 85.3783 | 0 | 0 | 6 | HAUL ROAD | 0 | 3114
2024-12-18 | 20:45 | 21.924 | 85.3782 | 5.24 | 0 | 6 | HAUL ROAD | 10.3148 | 3115
2024-12-18 | 20:45 | 21.924 | 85.3782 | 10.12 | 0 | 6 | HAUL ROAD | 0 | 3116
2024-12-18 | 20:45 | 21.924 | 85.3781 | 0 | 0 | 6 | HAUL ROAD | 10.3148 | 3117
2024-12-18 | 20:45 | 21.924 | 85.3781 | 0 | 0 | 6 | HAUL ROAD | 0 | 3118
2024-12-18 | 20:45 | 21.924 | 85.378 | 0 | 0 | 6 | HAUL ROAD | 10.3148 | 3119
2024-12-18 | 20:45 | 21.9239 | 85.3779 | 41.6 | 5.24 | 6 | HAUL ROAD | 15.1674 | 3120
2024-12-18 | 20:45 | 21.9239 | 85.3779 | 101.5 | 0 | 6 | HAUL ROAD | 0 | 3121
2024-12-18 | 20:45 | 21.9239 | 85.3779 | 79.7 | 1.39 | 6 | HAUL ROAD | 0 | 3122
2024-12-18 | 20:45 | 21.9238 | 85.3778 | 26.31 | 7.58 | 6 | HAUL ROAD | 15.1671 | 3123
2024-12-18 | 20:45 | 21.9238 | 85.3777 | 18.36 | 1.39 | 6 | HAUL ROAD | 10.3148 | 3124
2024-12-18 | 20:45 | 21.9238 | 85.3776 | 12.8 | 0 | 6 | HAUL ROAD | 10.3148 | 3125
2024-12-18 | 20:45 | 21.9237 | 85.3776 | 3.16 | 0 | 6 | HAUL ROAD | 11.1192 | 3126
2024-12-18 | 20:45 | 21.9237 | 85.3775 | 0 | 0 | 6 | HAUL ROAD | 10.3152 | 3127
2024-12-18 | 20:45 | 21.9236 | 85.3774 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 3128
2024-12-18 | 20:45 | 21.9236 | 85.3773 | 0 | 0 | 6 | HAUL ROAD | 10.3157 | 3129
2024-12-18 | 20:45 | 21.9235 | 85.3773 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 3130
2024-12-18 | 20:45 | 21.9235 | 85.3772 | 0 | 0 | 6 | HAUL ROAD | 10.3152 | 3131
2024-12-18 | 20:45 | 21.9234 | 85.3771 | 0 | 0 | 6 | HAUL ROAD | 15.1674 | 3132
2024-12-18 | 20:45 | 21.9234 | 85.3771 | 0 | 0 | 6 | HAUL ROAD | 0 | 3133
2024-12-18 | 20:46 | 21.9233 | 85.377 | 0 | 0 | 6 | HAUL ROAD | 15.1677 | 3134
2024-12-18 | 20:46 | 21.9233 | 85.377 | 0 | 0 | 6 | HAUL ROAD | 0 | 3135
2024-12-18 | 20:46 | 21.9233 | 85.3769 | 0 | 0 | 6 | HAUL ROAD | 10.3157 | 3136
2024-12-18 | 20:46 | 21.9232 | 85.3769 | 0 | 1.39 | 6 | HAUL ROAD | 11.1192 | 3137
2024-12-18 | 20:46 | 21.9231 | 85.3769 | 0 | 3.16 | 6 | HAUL ROAD | 11.1192 | 3138
2024-12-18 | 20:46 | 21.9231 | 85.377 | 0 | 0 | 6 | HAUL ROAD | 10.3161 | 3139
2024-12-18 | 20:46 | 21.9231 | 85.3771 | 0 | 1.39 | 6 | HAUL ROAD | 10.3161 | 3140
2024-12-18 | 20:46 | 21.9232 | 85.3771 | 0 | 7.58 | 6 | HAUL ROAD | 11.1192 | 3141
2024-12-18 | 20:46 | 21.9232 | 85.3772 | 0 | 7.58 | 6 | HAUL ROAD | 10.3152 | 3142
2024-12-18 | 20:46 | 21.9233 | 85.3773 | 0 | 12.8 | 4 | S9 (LMV) | 15.1674 | 3143
2024-12-18 | 20:46 | 21.9233 | 85.3774 | 1.39 | 21.12 | 4 | S9 (LMV) | 10.3157 | 3144
2024-12-18 | 20:46 | 21.9233 | 85.3774 | 3.16 | 26.31 | 4 | S9 (LMV) | 0 | 3145
2024-12-18 | 20:46 | 21.9234 | 85.3775 | 15.57 | 33.45 | 4 | S9 (LMV) | 15.1677 | 3146
2024-12-18 | 20:46 | 21.9234 | 85.3775 | 33.45 | 36.16 | 4 | S9 (LMV) | 0 | 3147
2024-12-18 | 20:46 | 21.9234 | 85.3776 | 44.32 | 15.57 | 6 | HAUL ROAD | 10.3152 | 3148
2024-12-18 | 20:46 | 21.9235 | 85.3776 | 30.73 | 26.31 | 4 | S9 (LMV) | 11.1192 | 3149
2024-12-18 | 20:46 | 21.9235 | 85.3776 | 38.88 | 15.57 | 4 | S9 (LMV) | 0 | 3150
2024-12-18 | 20:46 | 21.9236 | 85.3777 | 44.32 | 26.31 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3151
2024-12-18 | 20:46 | 21.9237 | 85.3777 | 57.92 | 26.31 | 4 | S9 (LMV) | 11.1192 | 3152
2024-12-18 | 20:46 | 21.9237 | 85.3778 | 60.64 | 33.45 | 6 | HAUL ROAD (TO GATE-1) | 10.3152 | 3153
2024-12-18 | 20:46 | 21.9238 | 85.3778 | 68.8 | 21.12 | 6 | HAUL ROAD (TO GATE-1) | 11.1192 | 3154
2024-12-18 | 20:46 | 21.9239 | 85.3778 | 38.88 | 7.58 | 6 | HAUL ROAD (TO GATE-1) | 11.1192 | 3155
2024-12-18 | 20:46 | 21.924 | 85.3779 | 26.31 | 3.16 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3156
2024-12-18 | 20:46 | 21.924 | 85.3779 | 26.31 | 0 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3157
2024-12-18 | 20:46 | 21.9241 | 85.378 | 3.16 | 0 | 6 | HAUL ROAD (TO GATE-1) | 15.1671 | 3158
2024-12-18 | 20:46 | 21.9241 | 85.3781 | 0 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 10.3152 | 3159
2024-12-18 | 20:46 | 21.9241 | 85.3781 | 0 | 5.24 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3160
2024-12-18 | 20:46 | 21.9241 | 85.3782 | 0 | 10.12 | 6 | HAUL ROAD (TO GATE-1) | 10.3152 | 3161
2024-12-18 | 20:46 | 21.924 | 85.3783 | 0 | 12.8 | 6 | HAUL ROAD (TO GATE-1) | 15.1671 | 3162
2024-12-18 | 20:46 | 21.924 | 85.3784 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 10.3148 | 3163
2024-12-18 | 20:47 | 21.9241 | 85.3784 | 0 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 11.1192 | 3164
2024-12-18 | 20:47 | 21.9241 | 85.3785 | 5.24 | 0 | 6 | HAUL ROAD (TO GATE-1) | 10.3152 | 3165
2024-12-18 | 20:47 | 21.9242 | 85.3785 | 26.31 | 0 | 6 | HAUL ROAD (TO GATE-1) | 11.1192 | 3166
2024-12-18 | 20:47 | 21.9243 | 85.3786 | 12.8 | 15.57 | 6 | HAUL ROAD (TO GATE-1) | 15.1671 | 3167
2024-12-18 | 20:47 | 21.9244 | 85.3786 | 7.58 | 10.12 | 6 | HAUL ROAD (TO GATE-1) | 11.1196 | 3168
2024-12-18 | 20:47 | 21.9245 | 85.3787 | 71.53 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 15.1671 | 3169
2024-12-18 | 20:47 | 21.9246 | 85.3788 | 15.57 | 7.58 | 6 | HAUL ROAD (TO GATE-1) | 15.1677 | 3170
2024-12-18 | 20:47 | 21.9247 | 85.3789 | 23.79 | 7.58 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3171
2024-12-18 | 20:47 | 21.9248 | 85.3789 | 52.48 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 11.12 | 3172
2024-12-18 | 20:47 | 21.9249 | 85.379 | 12.8 | 7.58 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3173
2024-12-18 | 20:47 | 21.925 | 85.3791 | 3.16 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3174
2024-12-18 | 20:47 | 21.9251 | 85.3792 | 12.8 | 0 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3175
2024-12-18 | 20:47 | 21.9252 | 85.3792 | 66.08 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 11.1196 | 3176
2024-12-18 | 20:47 | 21.9253 | 85.3793 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3177
2024-12-18 | 20:47 | 21.9254 | 85.3794 | 0 | 3.16 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3178
2024-12-18 | 20:47 | 21.9256 | 85.3794 | 63.36 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 22.239 | 3179
2024-12-18 | 20:47 | 21.9257 | 85.3795 | 0 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 15.1671 | 3180
2024-12-18 | 20:47 | 21.9258 | 85.3795 | 0 | 5.24 | 6 | HAUL ROAD (TO GATE-1) | 11.1192 | 3181
2024-12-18 | 20:47 | 21.9259 | 85.3795 | 74.25 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 11.1196 | 3182
2024-12-18 | 20:47 | 21.926 | 85.3796 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3183
2024-12-18 | 20:47 | 21.9261 | 85.3796 | 3.16 | 3.16 | 6 | HAUL ROAD (TO GATE-1) | 11.1192 | 3184
2024-12-18 | 20:47 | 21.9262 | 85.3796 | 26.31 | 0 | 6 | HAUL ROAD (TO GATE-1) | 11.1196 | 3185
2024-12-18 | 20:47 | 21.9263 | 85.3796 | 12.8 | 10.12 | 6 | HAUL ROAD (TO GATE-1) | 11.12 | 3186
2024-12-18 | 20:47 | 21.9265 | 85.3796 | 33.45 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 22.2392 | 3187
2024-12-18 | 20:47 | 21.9266 | 85.3796 | 38.88 | 3.16 | 6 | HAUL ROAD (TO GATE-1) | 11.1196 | 3188
2024-12-18 | 20:47 | 21.9267 | 85.3796 | 30.73 | 12.8 | 6 | HAUL ROAD (TO GATE-1) | 11.1192 | 3189
2024-12-18 | 20:47 | 21.9268 | 85.3796 | 44.32 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 11.1196 | 3190
2024-12-18 | 20:47 | 21.9269 | 85.3797 | 7.58 | 0 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3191
2024-12-18 | 20:47 | 21.927 | 85.3797 | 10.12 | 3.16 | 6 | HAUL ROAD (TO GATE-1) | 11.1192 | 3192
2024-12-18 | 20:47 | 21.9271 | 85.3797 | 15.57 | 3.16 | 6 | HAUL ROAD (TO GATE-1) | 11.12 | 3193
2024-12-18 | 20:48 | 21.9272 | 85.3797 | 18.36 | 7.58 | 6 | HAUL ROAD (TO GATE-1) | 11.1196 | 3194
2024-12-18 | 20:48 | 21.9273 | 85.3798 | 15.57 | 3.16 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3195
2024-12-18 | 20:48 | 21.9273 | 85.3798 | 21.12 | 5.24 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3196
2024-12-18 | 20:48 | 21.9274 | 85.3799 | 21.12 | 3.16 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3197
2024-12-18 | 20:48 | 21.9275 | 85.3799 | 30.73 | 3.16 | 6 | HAUL ROAD (TO GATE-1) | 11.1196 | 3198
2024-12-18 | 20:48 | 21.9275 | 85.38 | 33.45 | 0 | 6 | HAUL ROAD (TO GATE-1) | 10.3157 | 3199
2024-12-18 | 20:48 | 21.9276 | 85.3801 | 3.16 | 0 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3200
2024-12-18 | 20:48 | 21.9276 | 85.3801 | 3.16 | 0 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3201
2024-12-18 | 20:48 | 21.9277 | 85.3801 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 11.1196 | 3202
2024-12-18 | 20:48 | 21.9277 | 85.3801 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3203
2024-12-18 | 20:48 | 21.9277 | 85.3801 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3204
2024-12-18 | 20:48 | 21.9277 | 85.3801 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3205
2024-12-18 | 20:48 | 21.9277 | 85.3801 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3206
2024-12-18 | 20:48 | 21.9277 | 85.3801 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3207
2024-12-18 | 20:48 | 21.9277 | 85.3801 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3208
2024-12-18 | 20:48 | 21.9277 | 85.3801 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3209
2024-12-18 | 20:48 | 21.9277 | 85.3802 | 1.39 | 0 | 6 | HAUL ROAD (TO GATE-1) | 10.3152 | 3210
2024-12-18 | 20:48 | 21.9278 | 85.3802 | 1.39 | 0 | 6 | HAUL ROAD (TO GATE-1) | 11.1196 | 3211
2024-12-18 | 20:48 | 21.9279 | 85.3803 | 3.16 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 15.1671 | 3212
2024-12-18 | 20:48 | 21.9279 | 85.3803 | 30.73 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3213
2024-12-18 | 20:48 | 21.9279 | 85.3803 | 21.12 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3214
2024-12-18 | 20:48 | 21.928 | 85.3804 | 10.12 | 7.58 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3215
2024-12-18 | 20:48 | 21.928 | 85.3804 | 26.31 | 3.16 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3216
2024-12-18 | 20:48 | 21.9281 | 85.3804 | 30.73 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 11.1192 | 3217
2024-12-18 | 20:48 | 21.9281 | 85.3805 | 7.58 | 3.16 | 6 | HAUL ROAD (TO GATE-1) | 10.3148 | 3218
2024-12-18 | 20:48 | 21.9282 | 85.3805 | 21.12 | 0 | 6 | HAUL ROAD (TO GATE-1) | 11.1192 | 3219
2024-12-18 | 20:48 | 21.9282 | 85.3805 | 23.79 | 0 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3220
2024-12-18 | 20:48 | 21.9283 | 85.3806 | 3.16 | 0 | 6 | HAUL ROAD (TO GATE-1) | 15.1671 | 3221
2024-12-18 | 20:48 | 21.9283 | 85.3806 | 0 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3222
2024-12-18 | 20:48 | 21.9284 | 85.3807 | 0 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3223
2024-12-18 | 20:49 | 21.9284 | 85.3807 | 23.79 | 0 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3224
2024-12-18 | 20:49 | 21.9285 | 85.3808 | 10.12 | 0 | 6 | HAUL ROAD (TO GATE-1) | 15.1671 | 3225
2024-12-18 | 20:49 | 21.9285 | 85.3809 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 10.3152 | 3226
2024-12-18 | 20:49 | 21.9286 | 85.3809 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 11.1196 | 3227
2024-12-18 | 20:49 | 21.9286 | 85.381 | 0 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 10.3152 | 3228
2024-12-18 | 20:49 | 21.9287 | 85.3811 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3229
2024-12-18 | 20:49 | 21.9287 | 85.3811 | 1.39 | 5.24 | 6 | HAUL ROAD (TO GATE-1) | 0.094935 | 3230
2024-12-18 | 20:49 | 21.9288 | 85.3812 | 30.73 | 10.12 | 6 | HAUL ROAD (TO GATE-1) | 15.1671 | 3231
2024-12-18 | 20:49 | 21.9288 | 85.3812 | 49.76 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3232
2024-12-18 | 20:49 | 21.9289 | 85.3813 | 12.8 | 7.58 | 6 | HAUL ROAD (TO GATE-1) | 15.1671 | 3233
2024-12-18 | 20:49 | 21.9289 | 85.3813 | 60.64 | 7.58 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3234
2024-12-18 | 20:49 | 21.9289 | 85.3814 | 38.88 | 10.12 | 6 | HAUL ROAD (TO GATE-1) | 10.3152 | 3235
2024-12-18 | 20:49 | 21.929 | 85.3814 | 26.31 | 12.8 | 6 | HAUL ROAD (TO GATE-1) | 11.1196 | 3236
2024-12-18 | 20:49 | 21.929 | 85.3815 | 38.88 | 7.58 | 6 | HAUL ROAD (TO GATE-1) | 10.3148 | 3237
2024-12-18 | 20:49 | 21.929 | 85.3815 | 38.88 | 3.16 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3238
2024-12-18 | 20:49 | 21.9291 | 85.3816 | 5.24 | 5.24 | 6 | HAUL ROAD (TO GATE-1) | 15.1671 | 3239
2024-12-18 | 20:49 | 21.9291 | 85.3817 | 1.39 | 10.12 | 6 | HAUL ROAD (TO GATE-1) | 10.3148 | 3240
2024-12-18 | 20:49 | 21.9291 | 85.3817 | 5.24 | 12.8 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3241
2024-12-18 | 20:49 | 21.9292 | 85.3818 | 10.12 | 10.12 | 6 | HAUL ROAD (TO GATE-1) | 15.1674 | 3242
2024-12-18 | 20:49 | 21.9292 | 85.3818 | 12.8 | 3.16 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3243
2024-12-18 | 20:49 | 21.9293 | 85.3819 | 12.8 | 0 | 4 | S8 | 15.1671 | 3244
2024-12-18 | 20:49 | 21.9293 | 85.3819 | 10.12 | 0 | 4 | S8 | 0 | 3245
2024-12-18 | 20:49 | 21.9294 | 85.382 | 7.58 | 0 | 4 | S8 | 15.1674 | 3246
2024-12-18 | 20:49 | 21.9294 | 85.3821 | 1.39 | 1.39 | 4 | S8 | 10.3152 | 3247
2024-12-18 | 20:49 | 21.9295 | 85.3821 | 1.39 | 0 | 4 | S8 | 11.1196 | 3248
2024-12-18 | 20:49 | 21.9295 | 85.3822 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 10.3152 | 3249
2024-12-18 | 20:49 | 21.9295 | 85.3822 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3250
2024-12-18 | 20:49 | 21.9296 | 85.3822 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 11.1192 | 3251
2024-12-18 | 20:49 | 21.9296 | 85.3823 | 1.39 | 3.16 | 6 | HAUL ROAD (TO GATE-1) | 10.3148 | 3252
2024-12-18 | 20:49 | 21.9296 | 85.3823 | 7.58 | 5.24 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3253
2024-12-18 | 20:50 | 21.9297 | 85.3824 | 30.73 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 15.1668 | 3254
2024-12-18 | 20:50 | 21.9297 | 85.3824 | 23.79 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 0 | 3255
2024-12-18 | 20:50 | 21.9297 | 85.3825 | 12.8 | 7.58 | 6 | HAUL ROAD (TO GATE-1) | 10.3148 | 3256
2024-12-18 | 20:50 | 21.9297 | 85.3826 | 12.8 | 5.24 | 6 | HAUL ROAD (TO GATE-1) | 10.3148 | 3257
2024-12-18 | 20:50 | 21.9297 | 85.3827 | 76.97 | 15.57 | 6 | HAUL ROAD (TO GATE-1) | 10.3148 | 3258
2024-12-18 | 20:50 | 21.9298 | 85.3828 | 208.16 | 36.16 | 6 | HAUL ROAD (TO GATE-1) | 15.1671 | 3259
2024-12-18 | 20:50 | 21.9299 | 85.3828 | 167.07 | 15.57 | 6 | HAUL ROAD (TO GATE-1) | 11.12 | 3260
2024-12-18 | 20:50 | 21.9299 | 85.3829 | 219.14 | 12.8 | 6 | HAUL ROAD (TO GATE-1) | 10.3152 | 3261
2024-12-18 | 20:50 | 21.93 | 85.383 | 142.45 | 1.39 | 6 | HAUL ROAD (TO GATE-1) | 15.1671 | 3262
2024-12-18 | 20:50 | 21.93 | 85.3831 | 60.64 | 10.12 | 6 | HAUL ROAD (TO GATE-1) | 10.3152 | 3263
2024-12-18 | 20:50 | 21.93 | 85.3832 | 47.04 | 0 | 6 | HAUL ROAD (TO GATE-1) | 10.3152 | 3264
2024-12-18 | 20:50 | 21.93 | 85.3833 | 0 | 0 | 6 | HAUL ROAD (TO GATE-1) | 10.3152 | 3265
2024-12-18 | 20:50 | 21.9301 | 85.3834 | 12.8 | 5.24 | 6 | HAUL ROAD (TO GATE-1) | 15.1671 | 3266
2024-12-18 | 20:50 | 21.9301 | 85.3835 | 5.24 | 0 | 6 | HAUL ROAD (TO GATE-1) | 10.3152 | 3267
2024-12-18 | 20:50 | 21.9301 | 85.3836 | 3.16 | 5.24 | 6 | HAUL ROAD (TO GATE-1) | 10.3152 | 3268
2024-12-18 | 20:50 | 21.9301 | 85.3837 | 10.12 | 0 | 6 | HAUL ROAD | 10.3152 | 3269
2024-12-18 | 20:50 | 21.9302 | 85.3838 | 3.16 | 7.58 | 6 | HAUL ROAD | 15.1671 | 3270
2024-12-18 | 20:50 | 21.9302 | 85.3839 | 36.16 | 18.36 | 6 | HAUL ROAD | 10.3148 | 3271
2024-12-18 | 20:50 | 21.9302 | 85.384 | 71.53 | 0 | 6 | HAUL ROAD | 10.3148 | 3272
2024-12-18 | 20:50 | 21.9302 | 85.3841 | 7.58 | 5.24 | 6 | HAUL ROAD | 10.3148 | 3273
2024-12-18 | 20:50 | 21.9302 | 85.3842 | 5.24 | 10.12 | 6 | HAUL ROAD | 10.3148 | 3274
2024-12-18 | 20:50 | 21.9302 | 85.3843 | 10.12 | 12.8 | 6 | HAUL ROAD | 10.3148 | 3275
2024-12-18 | 20:50 | 21.9302 | 85.3843 | 10.12 | 15.57 | 6 | HAUL ROAD | 0 | 3276
2024-12-18 | 20:50 | 21.9302 | 85.3843 | 3.16 | 12.8 | 6 | HAUL ROAD | 0 | 3277
2024-12-18 | 20:50 | 21.9302 | 85.3843 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 3278
2024-12-18 | 20:50 | 21.9302 | 85.3843 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 3279
2024-12-18 | 20:50 | 21.9302 | 85.3843 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 3280
2024-12-18 | 20:50 | 21.9302 | 85.3843 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 3281
2024-12-18 | 20:50 | 21.9302 | 85.3843 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 3282
2024-12-18 | 20:50 | 21.9302 | 85.3843 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 3283
2024-12-18 | 20:51 | 21.9302 | 85.3843 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 3284
2024-12-18 | 20:51 | 21.9302 | 85.3843 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 3285
2024-12-18 | 20:51 | 21.9302 | 85.3843 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 3286
2024-12-18 | 20:51 | 21.9302 | 85.3843 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 3287
2024-12-18 | 20:51 | 21.9302 | 85.3844 | 3.16 | 10.12 | 6 | HAUL ROAD | 10.3148 | 3288
2024-12-18 | 20:51 | 21.9302 | 85.3844 | 1.39 | 10.12 | 6 | HAUL ROAD | 0 | 3289
2024-12-18 | 20:51 | 21.9302 | 85.3844 | 3.16 | 1.39 | 6 | HAUL ROAD | 0 | 3290
2024-12-18 | 20:51 | 21.9302 | 85.3845 | 55.2 | 1.39 | 6 | HAUL ROAD | 10.3148 | 3291
2024-12-18 | 20:51 | 21.9302 | 85.3845 | 12.8 | 1.39 | 6 | HAUL ROAD | 0 | 3292
2024-12-18 | 20:51 | 21.9302 | 85.3846 | 0 | 0 | 6 | HAUL ROAD | 10.3148 | 3293
2024-12-18 | 20:51 | 21.9301 | 85.3846 | 5.24 | 0 | 6 | HAUL ROAD | 11.1196 | 3294
2024-12-18 | 20:51 | 21.9301 | 85.3846 | 5.24 | 1.39 | 6 | HAUL ROAD | 0 | 3295
2024-12-18 | 20:51 | 21.9301 | 85.3846 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 3296
2024-12-18 | 20:51 | 21.9301 | 85.3846 | 0 | 7.58 | 6 | HAUL ROAD | 0 | 3297
2024-12-18 | 20:51 | 21.9301 | 85.3846 | 1.39 | 1.39 | 6 | HAUL ROAD | 0 | 3298
2024-12-18 | 20:51 | 21.9301 | 85.3846 | 3.16 | 1.39 | 6 | HAUL ROAD | 0 | 3299
2024-12-18 | 20:51 | 21.9301 | 85.3846 | 5.24 | 1.39 | 6 | HAUL ROAD | 0 | 3300
2024-12-18 | 20:51 | 21.9301 | 85.3846 | 3.16 | 5.24 | 6 | HAUL ROAD | 0 | 3301
2024-12-18 | 20:51 | 21.9301 | 85.3845 | 1.39 | 10.12 | 6 | HAUL ROAD | 10.3152 | 3302
2024-12-18 | 20:51 | 21.9302 | 85.3845 | 3.16 | 18.36 | 6 | HAUL ROAD | 11.1196 | 3303
2024-12-18 | 20:51 | 21.9302 | 85.3844 | 7.58 | 10.12 | 6 | HAUL ROAD | 10.3148 | 3304
2024-12-18 | 20:51 | 21.9302 | 85.3844 | 5.24 | 3.16 | 6 | HAUL ROAD | 0 | 3305
2024-12-18 | 20:51 | 21.9302 | 85.3844 | 5.24 | 3.16 | 6 | HAUL ROAD | 0 | 3306
2024-12-18 | 20:51 | 21.9302 | 85.3844 | 5.24 | 3.16 | 6 | HAUL ROAD | 0 | 3307
2024-12-18 | 20:51 | 21.9302 | 85.3844 | 7.58 | 12.8 | 6 | HAUL ROAD | 0 | 3308
2024-12-18 | 20:51 | 21.9302 | 85.3843 | 0 | 3.16 | 6 | HAUL ROAD | 10.3148 | 3309
2024-12-18 | 20:51 | 21.9302 | 85.3843 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 3310
2024-12-18 | 20:51 | 21.9302 | 85.3842 | 3.16 | 5.24 | 6 | HAUL ROAD | 10.3148 | 3311
2024-12-18 | 20:51 | 21.9302 | 85.3841 | 7.58 | 3.16 | 6 | HAUL ROAD | 10.3148 | 3312
2024-12-18 | 20:51 | 21.9302 | 85.384 | 5.24 | 7.58 | 6 | HAUL ROAD | 10.3148 | 3313
2024-12-18 | 20:52 | 21.9302 | 85.3839 | 23.79 | 21.12 | 6 | HAUL ROAD | 10.3148 | 3314
2024-12-18 | 20:52 | 21.9301 | 85.3838 | 76.97 | 0 | 6 | HAUL ROAD | 15.1671 | 3315
2024-12-18 | 20:52 | 21.9301 | 85.3837 | 10.12 | 3.16 | 6 | HAUL ROAD | 10.3152 | 3316
2024-12-18 | 20:52 | 21.9301 | 85.3836 | 3.16 | 5.24 | 6 | HAUL ROAD | 10.3152 | 3317
2024-12-18 | 20:52 | 21.9301 | 85.3835 | 3.16 | 1.39 | 6 | HAUL ROAD | 10.3152 | 3318
2024-12-18 | 20:52 | 21.93 | 85.3834 | 3.16 | 5.24 | 6 | HAUL ROAD | 15.1671 | 3319
2024-12-18 | 20:52 | 21.93 | 85.3833 | 21.12 | 7.58 | 6 | HAUL ROAD | 10.3152 | 3320
2024-12-18 | 20:52 | 21.93 | 85.3831 | 12.8 | 26.31 | 6 | HAUL ROAD | 20.63 | 3321
2024-12-18 | 20:52 | 21.93 | 85.383 | 63.36 | 57.92 | 6 | HAUL ROAD | 10.3152 | 3322
2024-12-18 | 20:52 | 21.9299 | 85.3829 | 98.77 | 74.25 | 6 | HAUL ROAD | 15.1671 | 3323
2024-12-18 | 20:52 | 21.9299 | 85.3828 | 221.88 | 47.04 | 6 | HAUL ROAD | 10.3152 | 3324
2024-12-18 | 20:52 | 21.9298 | 85.3828 | 197.19 | 10.12 | 6 | HAUL ROAD | 11.12 | 3325
2024-12-18 | 20:52 | 21.9298 | 85.3827 | 136.99 | 26.31 | 6 | HAUL ROAD | 10.3152 | 3326
2024-12-18 | 20:52 | 21.9297 | 85.3826 | 186.23 | 21.12 | 6 | HAUL ROAD | 15.1671 | 3327
2024-12-18 | 20:52 | 21.9297 | 85.3825 | 30.73 | 5.24 | 6 | HAUL ROAD | 10.3148 | 3328
2024-12-18 | 20:52 | 21.9297 | 85.3824 | 7.58 | 10.12 | 6 | HAUL ROAD | 10.3148 | 3329
2024-12-18 | 20:52 | 21.9297 | 85.3824 | 12.8 | 15.57 | 6 | HAUL ROAD | 0 | 3330
2024-12-18 | 20:52 | 21.9297 | 85.3823 | 26.31 | 23.79 | 6 | HAUL ROAD | 10.3148 | 3331
2024-12-18 | 20:52 | 21.9296 | 85.3823 | 26.31 | 12.8 | 6 | HAUL ROAD | 11.1192 | 3332
2024-12-18 | 20:52 | 21.9296 | 85.3823 | 18.36 | 3.16 | 6 | HAUL ROAD | 0 | 3333
2024-12-18 | 20:52 | 21.9295 | 85.3824 | 15.57 | 3.16 | 6 | HAUL ROAD | 15.1671 | 3334
2024-12-18 | 20:52 | 21.9295 | 85.3824 | 12.8 | 5.24 | 6 | HAUL ROAD | 0 | 3335
2024-12-18 | 20:52 | 21.9295 | 85.3824 | 18.36 | 10.12 | 6 | HAUL ROAD | 0 | 3336
2024-12-18 | 20:52 | 21.9295 | 85.3825 | 36.16 | 23.79 | 6 | HAUL ROAD | 10.3152 | 3337
2024-12-18 | 20:52 | 21.9295 | 85.3826 | 47.04 | 3.16 | 6 | HAUL ROAD | 10.3152 | 3338
2024-12-18 | 20:52 | 21.9296 | 85.3827 | 47.04 | 7.58 | 6 | HAUL ROAD | 15.1671 | 3339
2024-12-18 | 20:52 | 21.9296 | 85.3828 | 30.73 | 0 | 6 | HAUL ROAD | 10.3148 | 3340
2024-12-18 | 20:52 | 21.9296 | 85.3829 | 57.92 | 26.31 | 6 | HAUL ROAD | 10.3148 | 3341
2024-12-18 | 20:52 | 21.9296 | 85.3829 | 93.32 | 0 | 6 | HAUL ROAD | 0 | 3342
2024-12-18 | 20:52 | 21.9296 | 85.383 | 33.45 | 0 | 6 | HAUL ROAD | 10.3148 | 3343
2024-12-18 | 20:53 | 21.9295 | 85.3831 | 44.32 | 3.16 | 6 | HAUL ROAD | 15.1671 | 3344
2024-12-18 | 20:53 | 21.9295 | 85.3831 | 23.79 | 0 | 6 | HAUL ROAD | 0 | 3345
2024-12-18 | 20:53 | 21.9294 | 85.3832 | 12.8 | 12.8 | 6 | HAUL ROAD | 15.1674 | 3346
2024-12-18 | 20:53 | 21.9293 | 85.3832 | 101.5 | 0 | 6 | HAUL ROAD | 11.1196 | 3347
2024-12-18 | 20:53 | 21.9292 | 85.3832 | 26.31 | 0 | 6 | HAUL ROAD | 11.1192 | 3348
2024-12-18 | 20:53 | 21.9291 | 85.3832 | 82.42 | 0 | 6 | HAUL ROAD | 11.1196 | 3349
2024-12-18 | 20:53 | 21.929 | 85.3832 | 21.12 | 3.16 | 6 | HAUL ROAD | 11.1192 | 3350
2024-12-18 | 20:53 | 21.929 | 85.3831 | 10.12 | 1.39 | 6 | HAUL ROAD | 10.3148 | 3351
2024-12-18 | 20:53 | 21.9289 | 85.3831 | 12.8 | 5.24 | 6 | HAUL ROAD | 11.1196 | 3352
2024-12-18 | 20:53 | 21.9289 | 85.383 | 26.31 | 15.57 | 6 | HAUL ROAD | 10.3152 | 3353
2024-12-18 | 20:53 | 21.9288 | 85.383 | 106.96 | 7.58 | 6 | HAUL ROAD | 11.1192 | 3354
2024-12-18 | 20:53 | 21.9287 | 85.383 | 60.64 | 26.31 | 6 | HAUL ROAD | 11.1192 | 3355
2024-12-18 | 20:53 | 21.9287 | 85.3829 | 109.68 | 3.16 | 6 | HAUL ROAD | 10.3157 | 3356
2024-12-18 | 20:53 | 21.9286 | 85.3829 | 36.16 | 10.12 | 6 | HAUL ROAD | 11.1196 | 3357
2024-12-18 | 20:53 | 21.9285 | 85.3828 | 49.76 | 3.16 | 6 | HAUL ROAD | 15.1674 | 3358
2024-12-18 | 20:53 | 21.9285 | 85.3828 | 26.31 | 1.39 | 6 | HAUL ROAD | 0 | 3359
2024-12-18 | 20:53 | 21.9284 | 85.3827 | 21.12 | 10.12 | 6 | HAUL ROAD | 15.1671 | 3360
2024-12-18 | 20:53 | 21.9283 | 85.3826 | 36.16 | 5.24 | 6 | HAUL ROAD | 15.1674 | 3361
2024-12-18 | 20:53 | 21.9283 | 85.3826 | 47.04 | 21.12 | 6 | HAUL ROAD | 0 | 3362
2024-12-18 | 20:53 | 21.9282 | 85.3825 | 93.32 | 21.12 | 6 | HAUL ROAD | 15.1671 | 3363
2024-12-18 | 20:53 | 21.9282 | 85.3825 | 98.77 | 23.79 | 6 | HAUL ROAD | 0 | 3364
2024-12-18 | 20:53 | 21.9282 | 85.3825 | 90.59 | 26.31 | 6 | HAUL ROAD | 0 | 3365
2024-12-18 | 20:53 | 21.9282 | 85.3825 | 93.32 | 23.79 | 6 | HAUL ROAD | 0 | 3366
2024-12-18 | 20:53 | 21.9281 | 85.3824 | 96.05 | 3.16 | 6 | HAUL ROAD | 15.1671 | 3367
2024-12-18 | 20:53 | 21.9281 | 85.3824 | 66.08 | 0 | 6 | HAUL ROAD | 0 | 3368
2024-12-18 | 20:53 | 21.928 | 85.3823 | 55.2 | 21.12 | 6 | HAUL ROAD | 15.1671 | 3369
2024-12-18 | 20:53 | 21.928 | 85.3823 | 82.42 | 5.24 | 6 | HAUL ROAD | 0 | 3370
2024-12-18 | 20:53 | 21.928 | 85.3823 | 150.65 | 0 | 6 | HAUL ROAD | 0 | 3371
2024-12-18 | 20:53 | 21.928 | 85.3823 | 147.92 | 0 | 6 | HAUL ROAD | 0 | 3372
2024-12-18 | 20:53 | 21.928 | 85.3823 | 139.72 | 0 | 6 | HAUL ROAD | 0 | 3373
2024-12-18 | 20:54 | 21.928 | 85.3823 | 93.32 | 0 | 6 | HAUL ROAD | 0 | 3374
2024-12-18 | 20:54 | 21.928 | 85.3823 | 82.42 | 18.36 | 6 | HAUL ROAD | 0 | 3375
2024-12-18 | 20:54 | 21.928 | 85.3823 | 74.25 | 23.79 | 6 | HAUL ROAD | 0 | 3376
2024-12-18 | 20:54 | 21.928 | 85.3823 | 74.25 | 23.79 | 6 | HAUL ROAD | 0 | 3377
2024-12-18 | 20:54 | 21.928 | 85.3823 | 74.25 | 23.79 | 6 | HAUL ROAD | 0 | 3378
2024-12-18 | 20:54 | 21.9281 | 85.3823 | 76.97 | 7.58 | 6 | HAUL ROAD | 11.1192 | 3379
2024-12-18 | 20:54 | 21.9281 | 85.3824 | 55.2 | 18.36 | 6 | HAUL ROAD | 10.3148 | 3380
2024-12-18 | 20:54 | 21.9282 | 85.3824 | 66.08 | 36.16 | 6 | HAUL ROAD | 11.1192 | 3381
2024-12-18 | 20:54 | 21.9282 | 85.3825 | 101.5 | 21.12 | 6 | HAUL ROAD | 10.3152 | 3382
2024-12-18 | 20:54 | 21.9282 | 85.3825 | 98.77 | 47.04 | 6 | HAUL ROAD | 0 | 3383
2024-12-18 | 20:54 | 21.9282 | 85.3825 | 109.68 | 33.45 | 6 | HAUL ROAD | 0 | 3384
2024-12-18 | 20:54 | 21.9282 | 85.3826 | 117.87 | 33.45 | 6 | HAUL ROAD | 10.3152 | 3385
2024-12-18 | 20:54 | 21.9283 | 85.3826 | 98.77 | 21.12 | 6 | HAUL ROAD | 11.1192 | 3386
2024-12-18 | 20:54 | 21.9284 | 85.3827 | 74.25 | 5.24 | 6 | HAUL ROAD | 15.1674 | 3387
2024-12-18 | 20:54 | 21.9284 | 85.3827 | 26.31 | 10.12 | 6 | HAUL ROAD | 0 | 3388
2024-12-18 | 20:54 | 21.9285 | 85.3828 | 30.73 | 7.58 | 6 | HAUL ROAD | 15.1671 | 3389
2024-12-18 | 20:54 | 21.9285 | 85.3828 | 10.12 | 23.79 | 6 | HAUL ROAD | 0 | 3390
2024-12-18 | 20:54 | 21.9286 | 85.3829 | 44.32 | 12.8 | 6 | HAUL ROAD | 15.1674 | 3391
2024-12-18 | 20:54 | 21.9287 | 85.3829 | 44.32 | 15.57 | 6 | HAUL ROAD | 11.1196 | 3392
2024-12-18 | 20:54 | 21.9288 | 85.383 | 87.87 | 15.57 | 6 | HAUL ROAD | 15.1671 | 3393
2024-12-18 | 20:54 | 21.9289 | 85.3831 | 60.64 | 26.31 | 6 | HAUL ROAD | 15.1671 | 3394
2024-12-18 | 20:54 | 21.9289 | 85.3831 | 26.31 | 0 | 6 | HAUL ROAD | 0 | 3395
2024-12-18 | 20:54 | 21.929 | 85.3832 | 7.58 | 0 | 6 | HAUL ROAD | 15.1674 | 3396
2024-12-18 | 20:54 | 21.9291 | 85.3832 | 10.12 | 7.58 | 6 | HAUL ROAD | 11.1192 | 3397
2024-12-18 | 20:54 | 21.9292 | 85.3832 | 44.32 | 15.57 | 6 | HAUL ROAD | 11.1196 | 3398
2024-12-18 | 20:54 | 21.9293 | 85.3832 | 47.04 | 1.39 | 6 | HAUL ROAD | 11.1192 | 3399
2024-12-18 | 20:54 | 21.9294 | 85.3832 | 74.25 | 18.36 | 6 | HAUL ROAD | 11.1196 | 3400
2024-12-18 | 20:54 | 21.9295 | 85.3831 | 38.88 | 5.24 | 6 | HAUL ROAD | 15.1674 | 3401
2024-12-18 | 20:54 | 21.9296 | 85.383 | 18.36 | 12.8 | 6 | HAUL ROAD | 15.1671 | 3402
2024-12-18 | 20:54 | 21.9296 | 85.383 | 55.2 | 7.58 | 6 | HAUL ROAD | 0 | 3403
2024-12-18 | 20:55 | 21.9296 | 85.3829 | 49.76 | 38.88 | 6 | HAUL ROAD | 10.3148 | 3404
2024-12-18 | 20:55 | 21.9296 | 85.3828 | 98.77 | 7.58 | 6 | HAUL ROAD | 10.3148 | 3405
2024-12-18 | 20:55 | 21.9296 | 85.3827 | 15.57 | 15.57 | 6 | HAUL ROAD | 10.3148 | 3406
2024-12-18 | 20:55 | 21.9295 | 85.3826 | 57.92 | 7.58 | 6 | HAUL ROAD | 15.1671 | 3407
2024-12-18 | 20:55 | 21.9295 | 85.3825 | 41.6 | 23.79 | 6 | HAUL ROAD | 10.3152 | 3408
2024-12-18 | 20:55 | 21.9295 | 85.3824 | 55.2 | 5.24 | 6 | HAUL ROAD | 10.3152 | 3409
2024-12-18 | 20:55 | 21.9295 | 85.3824 | 21.12 | 10.12 | 6 | HAUL ROAD | 0 | 3410
2024-12-18 | 20:55 | 21.9296 | 85.3823 | 12.8 | 3.16 | 6 | HAUL ROAD | 15.1671 | 3411
2024-12-18 | 20:55 | 21.9296 | 85.3823 | 15.57 | 10.12 | 6 | HAUL ROAD | 0 | 3412
2024-12-18 | 20:55 | 21.9296 | 85.3823 | 18.36 | 7.58 | 6 | HAUL ROAD | 0 | 3413
2024-12-18 | 20:55 | 21.9296 | 85.3823 | 26.31 | 5.24 | 6 | HAUL ROAD | 0 | 3414
2024-12-18 | 20:55 | 21.9296 | 85.3823 | 23.79 | 3.16 | 6 | HAUL ROAD | 0 | 3415
2024-12-18 | 20:55 | 21.9296 | 85.3823 | 26.31 | 5.24 | 6 | HAUL ROAD | 0 | 3416
2024-12-18 | 20:55 | 21.9296 | 85.3823 | 18.36 | 7.58 | 6 | HAUL ROAD | 0 | 3417
2024-12-18 | 20:55 | 21.9296 | 85.3824 | 15.57 | 10.12 | 6 | HAUL ROAD | 10.3148 | 3418
2024-12-18 | 20:55 | 21.9296 | 85.3824 | 12.8 | 10.12 | 6 | HAUL ROAD | 0 | 3419
2024-12-18 | 20:55 | 21.9295 | 85.3824 | 12.8 | 5.24 | 6 | HAUL ROAD | 11.1192 | 3420
2024-12-18 | 20:55 | 21.9295 | 85.3824 | 12.8 | 7.58 | 6 | HAUL ROAD | 0 | 3421
2024-12-18 | 20:55 | 21.9295 | 85.3823 | 12.8 | 7.58 | 6 | HAUL ROAD | 10.3152 | 3422
2024-12-18 | 20:55 | 21.9295 | 85.3823 | 7.58 | 3.16 | 6 | HAUL ROAD | 0 | 3423
2024-12-18 | 20:55 | 21.9295 | 85.3823 | 1.39 | 7.58 | 6 | HAUL ROAD | 0 | 3424
2024-12-18 | 20:55 | 21.9295 | 85.3823 | 5.24 | 10.12 | 6 | HAUL ROAD | 0 | 3425
2024-12-18 | 20:55 | 21.9294 | 85.3822 | 3.16 | 7.58 | 6 | HAUL ROAD | 15.1674 | 3426
2024-12-18 | 20:55 | 21.9294 | 85.3822 | 7.58 | 7.58 | 6 | HAUL ROAD | 0 | 3427
2024-12-18 | 20:55 | 21.9293 | 85.3821 | 3.16 | 7.58 | 6 | HAUL ROAD | 15.1674 | 3428
2024-12-18 | 20:55 | 21.9293 | 85.382 | 10.12 | 10.12 | 6 | HAUL ROAD | 10.3152 | 3429
2024-12-18 | 20:55 | 21.9292 | 85.382 | 18.36 | 1.39 | 6 | HAUL ROAD | 11.1192 | 3430
2024-12-18 | 20:55 | 21.9292 | 85.3819 | 23.79 | 0 | 6 | HAUL ROAD | 10.3152 | 3431
2024-12-18 | 20:55 | 21.9293 | 85.3819 | 10.12 | 1.39 | 4 | S8 | 11.1192 | 3432
2024-12-18 | 20:55 | 21.9293 | 85.3819 | 3.16 | 0 | 4 | S8 | 0 | 3433
2024-12-18 | 20:56 | 21.9294 | 85.3818 | 0 | 3.16 | 6 | HAUL ROAD | 15.1674 | 3434
2024-12-18 | 20:56 | 21.9294 | 85.3818 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 3435
2024-12-18 | 20:56 | 21.9295 | 85.3818 | 7.58 | 1.39 | 6 | HAUL ROAD | 11.1196 | 3436
2024-12-18 | 20:56 | 21.9295 | 85.3818 | 60.64 | 3.16 | 6 | HAUL ROAD | 0 | 3437
2024-12-18 | 20:56 | 21.9296 | 85.3818 | 112.41 | 3.16 | 6 | HAUL ROAD | 11.1192 | 3438
2024-12-18 | 20:56 | 21.9296 | 85.3818 | 36.16 | 0 | 6 | HAUL ROAD | 0 | 3439
2024-12-18 | 20:56 | 21.9296 | 85.3819 | 0 | 1.39 | 6 | HAUL ROAD | 10.3148 | 3440
2024-12-18 | 20:56 | 21.9296 | 85.3819 | 5.24 | 5.24 | 6 | HAUL ROAD | 0 | 3441
2024-12-18 | 20:56 | 21.9296 | 85.3819 | 15.57 | 12.8 | 6 | HAUL ROAD | 0 | 3442
2024-12-18 | 20:56 | 21.9295 | 85.3819 | 18.36 | 18.36 | 4 | S8 | 11.1192 | 3443
2024-12-18 | 20:56 | 21.9295 | 85.382 | 26.31 | 23.79 | 4 | S8 | 10.3152 | 3444
2024-12-18 | 20:56 | 21.9295 | 85.382 | 30.73 | 23.79 | 4 | S8 | 0 | 3445
2024-12-18 | 20:56 | 21.9295 | 85.382 | 26.31 | 7.58 | 4 | S8 | 0 | 3446
2024-12-18 | 20:56 | 21.9295 | 85.382 | 7.58 | 5.24 | 4 | S8 | 0 | 3447
2024-12-18 | 20:56 | 21.9295 | 85.3821 | 3.16 | 0 | 4 | S8 | 10.3152 | 3448
2024-12-18 | 20:56 | 21.9295 | 85.3821 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3449
2024-12-18 | 20:56 | 21.9295 | 85.3821 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3450
2024-12-18 | 20:56 | 21.9296 | 85.3822 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 15.1671 | 3451
2024-12-18 | 20:56 | 21.9296 | 85.3822 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3452
2024-12-18 | 20:56 | 21.9296 | 85.3822 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3453
2024-12-18 | 20:56 | 21.9296 | 85.3823 | 1.39 | 3.16 | 6 | HAUL ROAD (TO ADMIN) | 10.3148 | 3454
2024-12-18 | 20:56 | 21.9297 | 85.3823 | 7.58 | 7.58 | 6 | HAUL ROAD (TO ADMIN) | 11.1192 | 3455
2024-12-18 | 20:56 | 21.9297 | 85.3823 | 18.36 | 1.39 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3456
2024-12-18 | 20:56 | 21.9297 | 85.3823 | 15.57 | 3.16 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3457
2024-12-18 | 20:56 | 21.9297 | 85.3823 | 18.36 | 1.39 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3458
2024-12-18 | 20:56 | 21.9298 | 85.3823 | 12.8 | 12.8 | 6 | HAUL ROAD (TO ADMIN) | 11.1196 | 3459
2024-12-18 | 20:56 | 21.9298 | 85.3823 | 10.12 | 15.57 | 6 | HAUL ROAD (TO ADMIN) | 0.094935 | 3460
2024-12-18 | 20:56 | 21.9298 | 85.3823 | 7.58 | 10.12 | 6 | HAUL ROAD (TO ADMIN) | 0.094935 | 3461
2024-12-18 | 20:56 | 21.9299 | 85.3823 | 1.39 | 5.24 | 6 | HAUL ROAD (TO ADMIN) | 11.12 | 3462
2024-12-18 | 20:56 | 21.9299 | 85.3822 | 3.16 | 12.8 | 6 | HAUL ROAD (TO ADMIN) | 10.3152 | 3463
2024-12-18 | 20:57 | 21.9299 | 85.3822 | 3.16 | 18.36 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3464
2024-12-18 | 20:57 | 21.93 | 85.3822 | 1.39 | 10.12 | 6 | HAUL ROAD (TO ADMIN) | 11.1196 | 3465
2024-12-18 | 20:57 | 21.93 | 85.3821 | 3.16 | 0 | 6 | HAUL ROAD (TO ADMIN) | 10.3152 | 3466
2024-12-18 | 20:57 | 21.9301 | 85.3821 | 0 | 3.16 | 6 | HAUL ROAD (TO ADMIN) | 11.1196 | 3467
2024-12-18 | 20:57 | 21.9301 | 85.382 | 0 | 7.58 | 6 | HAUL ROAD (TO ADMIN) | 10.3152 | 3468
2024-12-18 | 20:57 | 21.9302 | 85.382 | 0 | 7.58 | 6 | HAUL ROAD (TO ADMIN) | 11.1196 | 3469
2024-12-18 | 20:57 | 21.9302 | 85.3819 | 3.16 | 5.24 | 6 | HAUL ROAD (TO ADMIN) | 10.3148 | 3470
2024-12-18 | 20:57 | 21.9302 | 85.3819 | 0 | 3.16 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3471
2024-12-18 | 20:57 | 21.9303 | 85.3818 | 1.39 | 3.16 | 6 | HAUL ROAD (TO ADMIN) | 15.1671 | 3472
2024-12-18 | 20:57 | 21.9304 | 85.3818 | 0 | 10.12 | 6 | HAUL ROAD (TO ADMIN) | 11.1192 | 3473
2024-12-18 | 20:57 | 21.9304 | 85.3817 | 0 | 3.16 | 6 | HAUL ROAD (TO ADMIN) | 10.3148 | 3474
2024-12-18 | 20:57 | 21.9305 | 85.3817 | 0 | 5.24 | 6 | HAUL ROAD (TO ADMIN) | 11.1196 | 3475
2024-12-18 | 20:57 | 21.9306 | 85.3816 | 76.97 | 55.2 | 6 | HAUL ROAD (TO ADMIN) | 15.1671 | 3476
2024-12-18 | 20:57 | 21.9307 | 85.3816 | 21.12 | 3.16 | 6 | HAUL ROAD (TO ADMIN) | 11.1192 | 3477
2024-12-18 | 20:57 | 21.9309 | 85.3815 | 123.33 | 0 | 6 | HAUL ROAD (TO ADMIN) | 24.5146 | 3478
2024-12-18 | 20:57 | 21.931 | 85.3815 | 93.32 | 12.8 | 6 | HAUL ROAD (TO ADMIN) | 11.12 | 3479
2024-12-18 | 20:57 | 21.9311 | 85.3814 | 21.12 | 38.88 | 4 | S4 | 15.1671 | 3480
2024-12-18 | 20:57 | 21.9312 | 85.3814 | 60.64 | 10.12 | 6 | HAUL ROAD (TO ADMIN) | 11.1196 | 3481
2024-12-18 | 20:57 | 21.9313 | 85.3813 | 112.41 | 57.92 | 4 | S5 | 15.1671 | 3482
2024-12-18 | 20:57 | 21.9314 | 85.3812 | 49.76 | 52.48 | 6 | HAUL ROAD (TO ADMIN) | 15.1671 | 3483
2024-12-18 | 20:57 | 21.9315 | 85.3812 | 66.08 | 5.24 | 6 | HAUL ROAD (TO ADMIN) | 11.12 | 3484
2024-12-18 | 20:57 | 21.9316 | 85.3811 | 147.92 | 36.16 | 6 | HAUL ROAD (TO ADMIN) | 15.1671 | 3485
2024-12-18 | 20:57 | 21.9316 | 85.3811 | 21.12 | 0 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3486
2024-12-18 | 20:57 | 21.9317 | 85.3811 | 44.32 | 0 | 6 | HAUL ROAD (TO ADMIN) | 11.1196 | 3487
2024-12-18 | 20:57 | 21.9317 | 85.3812 | 93.32 | 0 | 6 | HAUL ROAD (TO ADMIN) | 10.3148 | 3488
2024-12-18 | 20:57 | 21.9317 | 85.3813 | 90.59 | 1.39 | 6 | HAUL ROAD (TO ADMIN) | 10.3148 | 3489
2024-12-18 | 20:57 | 21.9317 | 85.3813 | 44.32 | 7.58 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3490
2024-12-18 | 20:57 | 21.9317 | 85.3815 | 41.6 | 10.12 | 6 | HAUL ROAD (TO ADMIN) | 20.6296 | 3491
2024-12-18 | 20:57 | 21.9317 | 85.3816 | 47.04 | 7.58 | 6 | HAUL ROAD (TO ADMIN) | 10.3148 | 3492
2024-12-18 | 20:57 | 21.9317 | 85.3816 | 23.79 | 12.8 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3493
2024-12-18 | 20:58 | 21.9317 | 85.3817 | 41.6 | 10.12 | 6 | HAUL ROAD (TO ADMIN) | 10.3148 | 3494
2024-12-18 | 20:58 | 21.9317 | 85.3818 | 30.73 | 10.12 | 6 | HAUL ROAD (TO ADMIN) | 10.3148 | 3495
2024-12-18 | 20:58 | 21.9317 | 85.3818 | 5.24 | 1.39 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3496
2024-12-18 | 20:58 | 21.9318 | 85.3819 | 1.39 | 10.12 | 6 | HAUL ROAD (TO ADMIN) | 15.1671 | 3497
2024-12-18 | 20:58 | 21.9318 | 85.3819 | 7.58 | 18.36 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3498
2024-12-18 | 20:58 | 21.9319 | 85.382 | 23.79 | 12.8 | 6 | HAUL ROAD (TO ADMIN) | 15.1671 | 3499
2024-12-18 | 20:58 | 21.932 | 85.382 | 1.39 | 5.24 | 6 | HAUL ROAD (TO ADMIN) | 11.1196 | 3500
2024-12-18 | 20:58 | 21.932 | 85.382 | 3.16 | 7.58 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3501
2024-12-18 | 20:58 | 21.9321 | 85.382 | 10.12 | 10.12 | 6 | HAUL ROAD (TO ADMIN) | 11.1196 | 3502
2024-12-18 | 20:58 | 21.9321 | 85.382 | 12.8 | 7.58 | 6 | HAUL ROAD (TO ADMIN) | 0.094935 | 3503
2024-12-18 | 20:58 | 21.9322 | 85.3819 | 18.36 | 1.39 | 6 | HAUL ROAD (TO ADMIN) | 15.1671 | 3504
2024-12-18 | 20:58 | 21.9322 | 85.3818 | 18.36 | 0 | 6 | HAUL ROAD (TO ADMIN) | 10.3152 | 3505
2024-12-18 | 20:58 | 21.9323 | 85.3818 | 7.58 | 3.16 | 6 | HAUL ROAD (TO ADMIN) | 11.12 | 3506
2024-12-18 | 20:58 | 21.9323 | 85.3817 | 5.24 | 1.39 | 6 | HAUL ROAD (TO ADMIN) | 10.3152 | 3507
2024-12-18 | 20:58 | 21.9324 | 85.3816 | 0 | 3.16 | 6 | HAUL ROAD (TO ADMIN) | 15.1671 | 3508
2024-12-18 | 20:58 | 21.9324 | 85.3816 | 0 | 3.16 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3509
2024-12-18 | 20:58 | 21.9325 | 85.3815 | 0 | 5.24 | 6 | HAUL ROAD (TO ADMIN) | 15.1671 | 3510
2024-12-18 | 20:58 | 21.9325 | 85.3815 | 0 | 5.24 | 6 | HAUL ROAD (TO ADMIN) | 0.094935 | 3511
2024-12-18 | 20:58 | 21.9326 | 85.3814 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 15.1671 | 3512
2024-12-18 | 20:58 | 21.9326 | 85.3814 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3513
2024-12-18 | 20:58 | 21.9327 | 85.3814 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 11.1192 | 3514
2024-12-18 | 20:58 | 21.9327 | 85.3815 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 10.3148 | 3515
2024-12-18 | 20:58 | 21.9328 | 85.3815 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 11.1192 | 3516
2024-12-18 | 20:58 | 21.9328 | 85.3816 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 10.3144 | 3517
2024-12-18 | 20:58 | 21.9329 | 85.3817 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 15.1671 | 3518
2024-12-18 | 20:58 | 21.9329 | 85.3817 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3519
2024-12-18 | 20:58 | 21.933 | 85.3818 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 15.1671 | 3520
2024-12-18 | 20:58 | 21.933 | 85.3818 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 0.094935 | 3521
2024-12-18 | 20:58 | 21.9331 | 85.3818 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 11.1196 | 3522
2024-12-18 | 20:58 | 21.9332 | 85.3819 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 15.1671 | 3523
2024-12-18 | 20:59 | 21.9332 | 85.3819 | 0 | 1.39 | 6 | HAUL ROAD (TO ADMIN) | 0.094935 | 3524
2024-12-18 | 20:59 | 21.9333 | 85.382 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 15.1671 | 3525
2024-12-18 | 20:59 | 21.9334 | 85.382 | 5.24 | 1.39 | 6 | HAUL ROAD (TO ADMIN) | 11.1196 | 3526
2024-12-18 | 20:59 | 21.9334 | 85.3821 | 7.58 | 1.39 | 6 | HAUL ROAD (TO ADMIN) | 10.3148 | 3527
2024-12-18 | 20:59 | 21.9335 | 85.3821 | 18.36 | 1.39 | 6 | HAUL ROAD (TO ADMIN) | 11.1192 | 3528
2024-12-18 | 20:59 | 21.9335 | 85.3822 | 30.73 | 1.39 | 6 | HAUL ROAD (TO ADMIN) | 10.3144 | 3529
2024-12-18 | 20:59 | 21.9336 | 85.3822 | 47.04 | 0 | 6 | HAUL ROAD (TO ADMIN) | 11.1192 | 3530
2024-12-18 | 20:59 | 21.9336 | 85.3823 | 90.59 | 0 | 6 | HAUL ROAD (TO ADMIN) | 10.3148 | 3531
2024-12-18 | 20:59 | 21.9336 | 85.3824 | 76.97 | 0 | 6 | HAUL ROAD (TO ADMIN) | 10.3148 | 3532
2024-12-18 | 20:59 | 21.9336 | 85.3824 | 60.64 | 0 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3533
2024-12-18 | 20:59 | 21.9336 | 85.3825 | 60.64 | 0 | 6 | HAUL ROAD (TO ADMIN) | 10.3148 | 3534
2024-12-18 | 20:59 | 21.9336 | 85.3825 | 63.36 | 0 | 6 | HAUL ROAD (TO ADMIN) | 0 | 3535
2024-12-18 | 20:59 | 21.9335 | 85.3826 | 38.88 | 0 | 6 | HAUL ROAD (TO ADMIN) | 15.1668 | 3536
2024-12-18 | 20:59 | 21.9335 | 85.3827 | 21.12 | 0 | 6 | HAUL ROAD (TO ADMIN) | 10.3144 | 3537
2024-12-18 | 20:59 | 21.9334 | 85.3827 | 18.36 | 0 | 6 | HAUL ROAD (TO ADMIN) | 11.1192 | 3538
2024-12-18 | 20:59 | 21.9333 | 85.3827 | 12.8 | 0 | 6 | HAUL ROAD (TO ADMIN) | 11.1196 | 3539
2024-12-18 | 20:59 | 21.9333 | 85.3828 | 1.39 | 0 | 6 | HAUL ROAD (TO ADMIN) | 10.3144 | 3540
2024-12-18 | 20:59 | 21.9332 | 85.3828 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 11.1196 | 3541
2024-12-18 | 20:59 | 21.9332 | 85.3829 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 10.3152 | 3542
2024-12-18 | 20:59 | 21.9331 | 85.3829 | 0 | 0 | 6 | HAUL ROAD (TO ADMIN) | 11.1196 | 3543
2024-12-18 | 20:59 | 21.9331 | 85.3829 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3544
2024-12-18 | 20:59 | 21.933 | 85.3829 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3545
2024-12-18 | 20:59 | 21.9329 | 85.3829 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3546
2024-12-18 | 20:59 | 21.9329 | 85.3829 | 0 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3547
2024-12-18 | 20:59 | 21.9328 | 85.3829 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1192 | 3548
2024-12-18 | 20:59 | 21.9327 | 85.3829 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1192 | 3549
2024-12-18 | 20:59 | 21.9327 | 85.3828 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3550
2024-12-18 | 20:59 | 21.9326 | 85.3828 | 0 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1192 | 3551
2024-12-18 | 20:59 | 21.9325 | 85.3828 | 0 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3552
2024-12-18 | 20:59 | 21.9325 | 85.3828 | 0 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3553
2024-12-18 | 21:00 | 21.9324 | 85.3828 | 0 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3554
2024-12-18 | 21:00 | 21.9323 | 85.3828 | 0 | 10.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3555
2024-12-18 | 21:00 | 21.9323 | 85.3828 | 0 | 12.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3556
2024-12-18 | 21:00 | 21.9322 | 85.3828 | 3.16 | 38.88 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.12 | 3557
2024-12-18 | 21:00 | 21.9321 | 85.3827 | 30.73 | 98.77 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3558
2024-12-18 | 21:00 | 21.9321 | 85.3827 | 68.8 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3559
2024-12-18 | 21:00 | 21.9321 | 85.3826 | 3.16 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3152 | 3560
2024-12-18 | 21:00 | 21.9321 | 85.3825 | 3.16 | 10.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3152 | 3561
2024-12-18 | 21:00 | 21.9321 | 85.3824 | 15.57 | 18.36 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3152 | 3562
2024-12-18 | 21:00 | 21.9321 | 85.3823 | 33.45 | 26.31 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3152 | 3563
2024-12-18 | 21:00 | 21.9322 | 85.3822 | 52.48 | 26.31 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3564
2024-12-18 | 21:00 | 21.9322 | 85.3821 | 74.25 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3152 | 3565
2024-12-18 | 21:00 | 21.9321 | 85.3821 | 52.48 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3566
2024-12-18 | 21:00 | 21.9321 | 85.3821 | 23.79 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3567
2024-12-18 | 21:00 | 21.932 | 85.382 | 7.58 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3568
2024-12-18 | 21:00 | 21.9319 | 85.382 | 1.39 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3569
2024-12-18 | 21:00 | 21.9319 | 85.3819 | 0 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3152 | 3570
2024-12-18 | 21:00 | 21.9318 | 85.3819 | 15.57 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3571
2024-12-18 | 21:00 | 21.9317 | 85.3818 | 3.16 | 15.57 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3572
2024-12-18 | 21:00 | 21.9317 | 85.3818 | 7.58 | 10.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3573
2024-12-18 | 21:00 | 21.9316 | 85.3817 | 26.31 | 21.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3574
2024-12-18 | 21:00 | 21.9316 | 85.3816 | 90.59 | 30.73 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3575
2024-12-18 | 21:00 | 21.9317 | 85.3814 | 38.88 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 23.4356 | 3576
2024-12-18 | 21:00 | 21.9317 | 85.3813 | 117.87 | 23.79 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3577
2024-12-18 | 21:00 | 21.9317 | 85.3812 | 26.31 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3578
2024-12-18 | 21:00 | 21.9318 | 85.3811 | 115.14 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3579
2024-12-18 | 21:00 | 21.9318 | 85.381 | 18.36 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3580
2024-12-18 | 21:00 | 21.9318 | 85.3809 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3581
2024-12-18 | 21:00 | 21.9318 | 85.3808 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3582
2024-12-18 | 21:00 | 21.9319 | 85.3806 | 10.12 | 18.36 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 23.4356 | 3583
2024-12-18 | 21:01 | 21.9319 | 85.3806 | 1.39 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3584
2024-12-18 | 21:01 | 21.932 | 85.3805 | 0 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3585
2024-12-18 | 21:01 | 21.9321 | 85.3804 | 1.39 | 10.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3586
2024-12-18 | 21:01 | 21.9321 | 85.3804 | 5.24 | 21.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3587
2024-12-18 | 21:01 | 21.9321 | 85.3803 | 38.88 | 21.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3152 | 3588
2024-12-18 | 21:01 | 21.9321 | 85.3802 | 3.16 | 15.57 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3152 | 3589
2024-12-18 | 21:01 | 21.9321 | 85.3801 | 7.58 | 26.31 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3152 | 3590
2024-12-18 | 21:01 | 21.9321 | 85.38 | 21.12 | 26.31 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3152 | 3591
2024-12-18 | 21:01 | 21.932 | 85.38 | 23.79 | 21.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3592
2024-12-18 | 21:01 | 21.9319 | 85.3799 | 7.58 | 12.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3593
2024-12-18 | 21:01 | 21.9319 | 85.3798 | 5.24 | 12.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3152 | 3594
2024-12-18 | 21:01 | 21.9319 | 85.3798 | 5.24 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3595
2024-12-18 | 21:01 | 21.932 | 85.3797 | 7.58 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3596
2024-12-18 | 21:01 | 21.932 | 85.3797 | 7.58 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3597
2024-12-18 | 21:01 | 21.9321 | 85.3797 | 7.58 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3598
2024-12-18 | 21:01 | 21.9322 | 85.3797 | 12.8 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3599
2024-12-18 | 21:01 | 21.9323 | 85.3797 | 47.04 | 10.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.12 | 3600
2024-12-18 | 21:01 | 21.9324 | 85.3797 | 47.04 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3601
2024-12-18 | 21:01 | 21.9325 | 85.3798 | 15.57 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3602
2024-12-18 | 21:01 | 21.9326 | 85.3798 | 10.12 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3603
2024-12-18 | 21:01 | 21.9327 | 85.3798 | 18.36 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1192 | 3604
2024-12-18 | 21:01 | 21.9328 | 85.3799 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3605
2024-12-18 | 21:01 | 21.9329 | 85.38 | 7.58 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3606
2024-12-18 | 21:01 | 21.9329 | 85.38 | 10.12 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3607
2024-12-18 | 21:01 | 21.933 | 85.3801 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3608
2024-12-18 | 21:01 | 21.9331 | 85.3802 | 10.12 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3609
2024-12-18 | 21:01 | 21.9332 | 85.3802 | 5.24 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3610
2024-12-18 | 21:01 | 21.9333 | 85.3803 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3611
2024-12-18 | 21:01 | 21.9333 | 85.3804 | 12.8 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3612
2024-12-18 | 21:01 | 21.9334 | 85.3804 | 7.58 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3613
2024-12-18 | 21:02 | 21.9335 | 85.3805 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3614
2024-12-18 | 21:02 | 21.9336 | 85.3806 | 12.8 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3615
2024-12-18 | 21:02 | 21.9336 | 85.3807 | 5.24 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3616
2024-12-18 | 21:02 | 21.9337 | 85.3808 | 1.39 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3617
2024-12-18 | 21:02 | 21.9338 | 85.3808 | 5.24 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3618
2024-12-18 | 21:02 | 21.9338 | 85.3809 | 12.8 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3619
2024-12-18 | 21:02 | 21.9339 | 85.381 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3620
2024-12-18 | 21:02 | 21.934 | 85.3811 | 1.39 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3621
2024-12-18 | 21:02 | 21.9341 | 85.3811 | 7.58 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1192 | 3622
2024-12-18 | 21:02 | 21.9341 | 85.3812 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3623
2024-12-18 | 21:02 | 21.9342 | 85.3813 | 10.12 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3624
2024-12-18 | 21:02 | 21.9343 | 85.3814 | 10.12 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3625
2024-12-18 | 21:02 | 21.9344 | 85.3815 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3626
2024-12-18 | 21:02 | 21.9345 | 85.3815 | 10.12 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3627
2024-12-18 | 21:02 | 21.9345 | 85.3816 | 7.58 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3628
2024-12-18 | 21:02 | 21.9346 | 85.3817 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3629
2024-12-18 | 21:02 | 21.9347 | 85.3817 | 10.12 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1192 | 3630
2024-12-18 | 21:02 | 21.9348 | 85.3817 | 18.36 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3631
2024-12-18 | 21:02 | 21.9348 | 85.3817 | 7.58 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3632
2024-12-18 | 21:02 | 21.9349 | 85.3817 | 12.8 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.12 | 3633
2024-12-18 | 21:02 | 21.9349 | 85.3816 | 12.8 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3152 | 3634
2024-12-18 | 21:02 | 21.935 | 85.3816 | 1.39 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3635
2024-12-18 | 21:02 | 21.935 | 85.3814 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 20.6292 | 3636
2024-12-18 | 21:02 | 21.935 | 85.3813 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3637
2024-12-18 | 21:02 | 21.935 | 85.3812 | 1.39 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3638
2024-12-18 | 21:02 | 21.935 | 85.3811 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3639
2024-12-18 | 21:02 | 21.935 | 85.381 | 1.39 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3640
2024-12-18 | 21:02 | 21.935 | 85.3808 | 10.12 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 20.6292 | 3641
2024-12-18 | 21:02 | 21.935 | 85.3807 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3642
2024-12-18 | 21:02 | 21.9351 | 85.3806 | 0 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3643
2024-12-18 | 21:03 | 21.9351 | 85.3805 | 5.24 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3644
2024-12-18 | 21:03 | 21.9352 | 85.3804 | 33.45 | 18.36 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3645
2024-12-18 | 21:03 | 21.9353 | 85.3804 | 30.73 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1192 | 3646
2024-12-18 | 21:03 | 21.9354 | 85.3803 | 7.58 | 21.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3647
2024-12-18 | 21:03 | 21.9355 | 85.3802 | 36.16 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3648
2024-12-18 | 21:03 | 21.9356 | 85.3802 | 21.12 | 18.36 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3649
2024-12-18 | 21:03 | 21.9357 | 85.3802 | 60.64 | 26.31 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3650
2024-12-18 | 21:03 | 21.9358 | 85.3801 | 85.14 | 23.79 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3651
2024-12-18 | 21:03 | 21.9359 | 85.3801 | 109.68 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1192 | 3652
2024-12-18 | 21:03 | 21.936 | 85.3801 | 90.59 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3653
2024-12-18 | 21:03 | 21.9362 | 85.3802 | 44.32 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 24.5145 | 3654
2024-12-18 | 21:03 | 21.9363 | 85.3802 | 10.12 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1192 | 3655
2024-12-18 | 21:03 | 21.9363 | 85.3803 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3139 | 3656
2024-12-18 | 21:03 | 21.9364 | 85.3804 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3657
2024-12-18 | 21:03 | 21.9365 | 85.3804 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3658
2024-12-18 | 21:03 | 21.9366 | 85.3805 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3659
2024-12-18 | 21:03 | 21.9367 | 85.3806 | 1.39 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3660
2024-12-18 | 21:03 | 21.9368 | 85.3806 | 36.16 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1192 | 3661
2024-12-18 | 21:03 | 21.9368 | 85.3807 | 7.58 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3139 | 3662
2024-12-18 | 21:03 | 21.9369 | 85.3808 | 18.36 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3663
2024-12-18 | 21:03 | 21.937 | 85.3809 | 21.12 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3664
2024-12-18 | 21:03 | 21.9371 | 85.3809 | 3.16 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3665
2024-12-18 | 21:03 | 21.9372 | 85.381 | 26.31 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3666
2024-12-18 | 21:03 | 21.9373 | 85.3811 | 0 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3667
2024-12-18 | 21:03 | 21.9374 | 85.3812 | 10.12 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3668
2024-12-18 | 21:03 | 21.9375 | 85.3813 | 5.24 | 15.57 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3669
2024-12-18 | 21:03 | 21.9376 | 85.3813 | 63.36 | 12.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.12 | 3670
2024-12-18 | 21:03 | 21.9377 | 85.3814 | 33.45 | 18.36 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3671
2024-12-18 | 21:03 | 21.9378 | 85.3815 | 44.32 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3672
2024-12-18 | 21:03 | 21.9379 | 85.3816 | 55.2 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3673
2024-12-18 | 21:04 | 21.938 | 85.3817 | 41.6 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3674
2024-12-18 | 21:04 | 21.9381 | 85.3818 | 15.57 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3675
2024-12-18 | 21:04 | 21.9382 | 85.3818 | 10.12 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3676
2024-12-18 | 21:04 | 21.9383 | 85.3819 | 76.97 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3677
2024-12-18 | 21:04 | 21.9384 | 85.382 | 7.58 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3678
2024-12-18 | 21:04 | 21.9384 | 85.3821 | 60.64 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3679
2024-12-18 | 21:04 | 21.9385 | 85.3821 | 10.12 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3680
2024-12-18 | 21:04 | 21.9386 | 85.3822 | 15.57 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3681
2024-12-18 | 21:04 | 21.9386 | 85.3823 | 26.31 | 15.57 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3682
2024-12-18 | 21:04 | 21.9387 | 85.3824 | 60.64 | 10.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3683
2024-12-18 | 21:04 | 21.9388 | 85.3825 | 36.16 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3684
2024-12-18 | 21:04 | 21.9388 | 85.3826 | 44.32 | 10.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3139 | 3685
2024-12-18 | 21:04 | 21.9389 | 85.3827 | 57.92 | 12.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3686
2024-12-18 | 21:04 | 21.9389 | 85.3828 | 52.48 | 15.57 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3687
2024-12-18 | 21:04 | 21.939 | 85.3829 | 57.92 | 21.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3688
2024-12-18 | 21:04 | 21.9391 | 85.383 | 82.42 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3689
2024-12-18 | 21:04 | 21.9391 | 85.3831 | 15.57 | 12.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3690
2024-12-18 | 21:04 | 21.9392 | 85.3831 | 60.64 | 10.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3691
2024-12-18 | 21:04 | 21.9392 | 85.3832 | 26.31 | 12.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3692
2024-12-18 | 21:04 | 21.9393 | 85.3833 | 38.88 | 18.36 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3693
2024-12-18 | 21:04 | 21.9394 | 85.3834 | 38.88 | 12.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3694
2024-12-18 | 21:04 | 21.9394 | 85.3835 | 52.48 | 23.79 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3695
2024-12-18 | 21:04 | 21.9395 | 85.3836 | 60.64 | 18.36 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3696
2024-12-18 | 21:04 | 21.9395 | 85.3836 | 49.76 | 15.57 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3697
2024-12-18 | 21:04 | 21.9395 | 85.3837 | 44.32 | 12.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3698
2024-12-18 | 21:04 | 21.9396 | 85.3838 | 55.2 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3699
2024-12-18 | 21:04 | 21.9396 | 85.3839 | 63.36 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3700
2024-12-18 | 21:04 | 21.9396 | 85.384 | 55.2 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3701
2024-12-18 | 21:04 | 21.9395 | 85.3841 | 23.79 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3702
2024-12-18 | 21:04 | 21.9395 | 85.3842 | 7.58 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3703
2024-12-18 | 21:05 | 21.9394 | 85.3843 | 5.24 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1671 | 3704
2024-12-18 | 21:05 | 21.9394 | 85.3844 | 3.16 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3705
2024-12-18 | 21:05 | 21.9394 | 85.3844 | 10.12 | 12.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3706
2024-12-18 | 21:05 | 21.9394 | 85.3845 | 175.28 | 33.45 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3707
2024-12-18 | 21:05 | 21.9393 | 85.3846 | 82.42 | 12.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3708
2024-12-18 | 21:05 | 21.9393 | 85.3847 | 104.23 | 68.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3709
2024-12-18 | 21:05 | 21.9393 | 85.3848 | 219.14 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3710
2024-12-18 | 21:05 | 21.9394 | 85.3849 | 123.33 | 57.92 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3711
2024-12-18 | 21:05 | 21.9394 | 85.385 | 128.79 | 49.76 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3712
2024-12-18 | 21:05 | 21.9395 | 85.385 | 161.59 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.12 | 3713
2024-12-18 | 21:05 | 21.9395 | 85.3851 | 30.73 | 12.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3714
2024-12-18 | 21:05 | 21.9396 | 85.3852 | 128.79 | 66.08 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3715
2024-12-18 | 21:05 | 21.9396 | 85.3852 | 208.16 | 18.36 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3716
2024-12-18 | 21:05 | 21.9397 | 85.3853 | 85.14 | 60.64 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3717
2024-12-18 | 21:05 | 21.9397 | 85.3853 | 216.39 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3718
2024-12-18 | 21:05 | 21.9398 | 85.3854 | 87.87 | 71.53 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3719
2024-12-18 | 21:05 | 21.9398 | 85.3855 | 188.97 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3720
2024-12-18 | 21:05 | 21.9399 | 85.3855 | 96.05 | 74.25 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1192 | 3721
2024-12-18 | 21:05 | 21.9399 | 85.3856 | 210.9 | 21.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3722
2024-12-18 | 21:05 | 21.94 | 85.3857 | 82.42 | 23.79 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3723
2024-12-18 | 21:05 | 21.94 | 85.3857 | 145.18 | 71.53 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3724
2024-12-18 | 21:05 | 21.94 | 85.3858 | 142.45 | 49.76 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3725
2024-12-18 | 21:05 | 21.9401 | 85.3859 | 161.59 | 68.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3726
2024-12-18 | 21:05 | 21.9401 | 85.386 | 175.28 | 76.97 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3727
2024-12-18 | 21:05 | 21.9402 | 85.3861 | 194.45 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3728
2024-12-18 | 21:05 | 21.9402 | 85.3861 | 123.33 | 71.53 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3729
2024-12-18 | 21:05 | 21.9402 | 85.3862 | 197.19 | 10.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3139 | 3730
2024-12-18 | 21:05 | 21.9403 | 85.3863 | 79.7 | 52.48 | 19 | DUMPER TERMINAL PARKING | 15.1668 | 3731
2024-12-18 | 21:05 | 21.9403 | 85.3864 | 156.12 | 30.73 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3732
2024-12-18 | 21:05 | 21.9403 | 85.3864 | 112.41 | 44.32 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3733
2024-12-18 | 21:06 | 21.9404 | 85.3865 | 117.87 | 55.2 | 19 | DUMPER TERMINAL PARKING | 15.1668 | 3734
2024-12-18 | 21:06 | 21.9404 | 85.3866 | 180.75 | 21.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3735
2024-12-18 | 21:06 | 21.9405 | 85.3866 | 68.8 | 60.64 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3736
2024-12-18 | 21:06 | 21.9405 | 85.3867 | 191.71 | 18.36 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3148 | 3737
2024-12-18 | 21:06 | 21.9406 | 85.3867 | 112.41 | 60.64 | 9 | DUMPER TERMINAL PATHWAY | 11.1196 | 3738
2024-12-18 | 21:06 | 21.9407 | 85.3868 | 199.93 | 12.8 | 9 | DUMPER TERMINAL PATHWAY | 15.1665 | 3739
2024-12-18 | 21:06 | 21.9407 | 85.3869 | 112.41 | 55.2 | 9 | DUMPER TERMINAL PATHWAY | 10.3144 | 3740
2024-12-18 | 21:06 | 21.9408 | 85.3869 | 167.07 | 33.45 | 9 | DUMPER TERMINAL PATHWAY | 11.1192 | 3741
2024-12-18 | 21:06 | 21.9408 | 85.387 | 98.77 | 36.16 | 9 | DUMPER TERMINAL PATHWAY | 10.3139 | 3742
2024-12-18 | 21:06 | 21.9409 | 85.3871 | 167.07 | 38.88 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3743
2024-12-18 | 21:06 | 21.9409 | 85.3871 | 117.87 | 15.57 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3744
2024-12-18 | 21:06 | 21.941 | 85.3872 | 96.05 | 49.76 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1668 | 3745
2024-12-18 | 21:06 | 21.941 | 85.3872 | 167.07 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3746
2024-12-18 | 21:06 | 21.9411 | 85.3872 | 18.36 | 15.57 | 19 | DUMPER TERMINAL PARKING | 11.1192 | 3747
2024-12-18 | 21:06 | 21.9412 | 85.3872 | 10.12 | 30.73 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3748
2024-12-18 | 21:06 | 21.9413 | 85.3872 | 15.57 | 57.92 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1192 | 3749
2024-12-18 | 21:06 | 21.9414 | 85.3872 | 71.53 | 117.87 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3750
2024-12-18 | 21:06 | 21.9414 | 85.3872 | 44.32 | 23.79 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3751
2024-12-18 | 21:06 | 21.9415 | 85.3872 | 44.32 | 21.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1192 | 3752
2024-12-18 | 21:06 | 21.9416 | 85.3872 | 36.16 | 23.79 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1192 | 3753
2024-12-18 | 21:06 | 21.9416 | 85.3873 | 41.6 | 55.2 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3754
2024-12-18 | 21:06 | 21.9417 | 85.3873 | 44.32 | 41.6 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3755
2024-12-18 | 21:06 | 21.9417 | 85.3873 | 33.45 | 36.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3756
2024-12-18 | 21:06 | 21.9418 | 85.3873 | 26.31 | 63.36 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3757
2024-12-18 | 21:06 | 21.9418 | 85.3873 | 49.76 | 79.7 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3758
2024-12-18 | 21:06 | 21.9418 | 85.3873 | 23.79 | 33.45 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3759
2024-12-18 | 21:06 | 21.9418 | 85.3873 | 10.12 | 15.57 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3760
2024-12-18 | 21:06 | 21.9418 | 85.3873 | 10.12 | 15.57 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3761
2024-12-18 | 21:06 | 21.9418 | 85.3873 | 7.58 | 12.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3762
2024-12-18 | 21:06 | 21.9418 | 85.3874 | 3.16 | 10.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3139 | 3763
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 21.12 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3764
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 57.92 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3765
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 74.25 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3766
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 93.32 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3767
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3768
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3769
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3770
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3771
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3772
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3773
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3774
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3775
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 106.96 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3776
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3777
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3778
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3779
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3780
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3781
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 106.96 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3782
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3783
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3784
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3785
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3786
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 106.96 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3787
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 109.68 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3788
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 15.57 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3789
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 85.14 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3790
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 183.49 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3791
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 178.02 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3792
2024-12-18 | 21:07 | 21.9418 | 85.3874 | 139.72 | 68.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3793
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 44.32 | 30.73 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3794
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 12.8 | 33.45 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3795
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 10.12 | 219.14 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3796
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 5.24 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3797
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 1.39 | 104.23 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3798
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 0 | 68.8 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3799
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 0 | 87.87 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3800
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3801
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 0 | 153.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3802
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 60.64 | 123.33 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3803
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 30.73 | 112.41 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3804
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 93.32 | 10.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3805
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 57.92 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3806
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 112.41 | 15.57 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3807
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 15.57 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3808
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 208.16 | 47.04 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3809
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 3.16 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3810
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3811
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3812
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 7.58 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3813
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 7.58 | 18.36 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3814
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 18.36 | 128.79 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3815
2024-12-18 | 21:08 | 21.9418 | 85.3874 | 18.36 | 142.45 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3816
2024-12-18 | 21:08 | 21.9418 | 85.3873 | 10.12 | 30.73 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3139 | 3817
2024-12-18 | 21:08 | 21.9418 | 85.3873 | 12.8 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3818
2024-12-18 | 21:08 | 21.9418 | 85.3873 | 7.58 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3819
2024-12-18 | 21:08 | 21.9418 | 85.3873 | 0 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3820
2024-12-18 | 21:08 | 21.9418 | 85.3873 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3821
2024-12-18 | 21:08 | 21.9418 | 85.3872 | 0 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3139 | 3822
2024-12-18 | 21:08 | 21.9418 | 85.3872 | 5.24 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3823
2024-12-18 | 21:09 | 21.9419 | 85.3872 | 0 | 0 | 17 | REST SHELTER | 11.1196 | 3824
2024-12-18 | 21:09 | 21.9419 | 85.3872 | 0 | 26.31 | 17 | REST SHELTER | 0.094935 | 3825
2024-12-18 | 21:09 | 21.9419 | 85.3872 | 49.76 | 1.39 | 17 | REST SHELTER | 0.094935 | 3826
2024-12-18 | 21:09 | 21.9419 | 85.3872 | 3.16 | 30.73 | 17 | REST SHELTER | 0.094935 | 3827
2024-12-18 | 21:09 | 21.9419 | 85.3872 | 15.57 | 1.39 | 17 | REST SHELTER | 0.094935 | 3828
2024-12-18 | 21:09 | 21.9419 | 85.3872 | 0 | 0 | 17 | REST SHELTER | 0.094935 | 3829
2024-12-18 | 21:09 | 21.9419 | 85.3872 | 10.12 | 5.24 | 17 | REST SHELTER | 0.094935 | 3830
2024-12-18 | 21:09 | 21.942 | 85.3871 | 5.24 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3831
2024-12-18 | 21:09 | 21.942 | 85.3871 | 15.57 | 21.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3832
2024-12-18 | 21:09 | 21.942 | 85.3871 | 3.16 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3833
2024-12-18 | 21:09 | 21.942 | 85.3871 | 10.12 | 21.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3834
2024-12-18 | 21:09 | 21.942 | 85.3871 | 1.39 | 10.12 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3835
2024-12-18 | 21:09 | 21.942 | 85.387 | 21.12 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3139 | 3836
2024-12-18 | 21:09 | 21.942 | 85.387 | 30.73 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3837
2024-12-18 | 21:09 | 21.942 | 85.387 | 21.12 | 104.23 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3838
2024-12-18 | 21:09 | 21.942 | 85.387 | 57.92 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3839
2024-12-18 | 21:09 | 21.942 | 85.387 | 26.31 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3840
2024-12-18 | 21:09 | 21.9419 | 85.387 | 134.25 | 7.58 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3841
2024-12-18 | 21:09 | 21.9419 | 85.387 | 7.58 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3842
2024-12-18 | 21:09 | 21.9419 | 85.3869 | 3.16 | 0 | 16 | FIRST AID STATION | 10.3144 | 3843
2024-12-18 | 21:09 | 21.9419 | 85.3869 | 0 | 1.39 | 16 | FIRST AID STATION | 0.094935 | 3844
2024-12-18 | 21:09 | 21.9419 | 85.3869 | 1.39 | 1.39 | 16 | FIRST AID STATION | 0.094935 | 3845
2024-12-18 | 21:09 | 21.9419 | 85.3869 | 3.16 | 3.16 | 16 | FIRST AID STATION | 0.094935 | 3846
2024-12-18 | 21:09 | 21.9419 | 85.3869 | 0 | 5.24 | 16 | FIRST AID STATION | 0.094935 | 3847
2024-12-18 | 21:09 | 21.9419 | 85.3869 | 0 | 3.16 | 16 | FIRST AID STATION | 0.094935 | 3848
2024-12-18 | 21:09 | 21.9419 | 85.3869 | 18.36 | 3.16 | 16 | FIRST AID STATION | 0.094935 | 3849
2024-12-18 | 21:09 | 21.9419 | 85.3869 | 0 | 1.39 | 16 | FIRST AID STATION | 0.094935 | 3850
2024-12-18 | 21:09 | 21.9419 | 85.3869 | 23.79 | 15.57 | 16 | FIRST AID STATION | 0.094935 | 3851
2024-12-18 | 21:09 | 21.9419 | 85.3869 | 12.8 | 0 | 16 | FIRST AID STATION | 0.094935 | 3852
2024-12-18 | 21:09 | 21.9419 | 85.3869 | 7.58 | 0 | 16 | FIRST AID STATION | 0.094935 | 3853
2024-12-18 | 21:10 | 21.9419 | 85.3869 | 1.39 | 0 | 16 | FIRST AID STATION | 0.094935 | 3854
2024-12-18 | 21:10 | 21.9419 | 85.3869 | 63.36 | 15.57 | 16 | FIRST AID STATION | 0.094935 | 3855
2024-12-18 | 21:10 | 21.9419 | 85.3869 | 5.24 | 0 | 16 | FIRST AID STATION | 0.094935 | 3856
2024-12-18 | 21:10 | 21.9419 | 85.3869 | 52.48 | 10.12 | 16 | FIRST AID STATION | 0.094935 | 3857
2024-12-18 | 21:10 | 21.9419 | 85.3869 | 26.31 | 0 | 16 | FIRST AID STATION | 0.094935 | 3858
2024-12-18 | 21:10 | 21.9419 | 85.3868 | 60.64 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 10.3144 | 3859
2024-12-18 | 21:10 | 21.9418 | 85.3868 | 5.24 | 1.39 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 11.1196 | 3860
2024-12-18 | 21:10 | 21.9418 | 85.3868 | 7.58 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3861
2024-12-18 | 21:10 | 21.9418 | 85.3868 | 5.24 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3862
2024-12-18 | 21:10 | 21.9418 | 85.3868 | 7.58 | 0 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3863
2024-12-18 | 21:10 | 21.9418 | 85.3868 | 26.31 | 3.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3864
2024-12-18 | 21:10 | 21.9418 | 85.3868 | 139.72 | 5.24 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0 | 3865
2024-12-18 | 21:10 | 21.9417 | 85.3867 | 12.8 | 49.76 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 15.1665 | 3866
2024-12-18 | 21:10 | 21.9417 | 85.3867 | 12.8 | 36.16 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3867
2024-12-18 | 21:10 | 21.9417 | 85.3867 | 12.8 | 18.36 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3868
2024-12-18 | 21:10 | 21.9417 | 85.3867 | 71.53 | 57.92 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3869
2024-12-18 | 21:10 | 21.9417 | 85.3867 | 115.14 | 55.2 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3870
2024-12-18 | 21:10 | 21.9417 | 85.3867 | 104.23 | 44.32 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3871
2024-12-18 | 21:10 | 21.9417 | 85.3867 | 128.79 | 96.05 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3872
2024-12-18 | 21:10 | 21.9417 | 85.3867 | 126.06 | 33.45 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3873
2024-12-18 | 21:10 | 21.9417 | 85.3867 | 145.18 | 18.36 | 6 | HAUL ROAD ( OLD EQUIPMENT TO GEM COMPLEX) | 0.094935 | 3874
2024-12-19 | 19:14 | 21.942 | 85.3873 | 7.58 | 15.57 | 17 | REST SHELTER | 70.3025 | 3875
2024-12-19 | 19:14 | 21.942 | 85.3873 | 18.36 | 44.32 | 17 | REST SHELTER | 0 | 3876
2024-12-19 | 19:14 | 21.942 | 85.3873 | 15.57 | 49.76 | 17 | REST SHELTER | 0 | 3877
2024-12-19 | 19:14 | 21.942 | 85.3873 | 21.12 | 76.97 | 17 | REST SHELTER | 0 | 3878
2024-12-19 | 19:14 | 21.942 | 85.3873 | 23.79 | 76.97 | 17 | REST SHELTER | 0 | 3879
2024-12-19 | 19:14 | 21.942 | 85.3873 | 23.79 | 76.97 | 17 | REST SHELTER | 0 | 3880
2024-12-19 | 19:14 | 21.942 | 85.3873 | 26.31 | 76.97 | 17 | REST SHELTER | 0 | 3881
2024-12-19 | 19:14 | 21.942 | 85.3873 | 26.31 | 76.97 | 17 | REST SHELTER | 0 | 3882
2024-12-19 | 19:14 | 21.942 | 85.3873 | 26.31 | 76.97 | 17 | REST SHELTER | 0 | 3883
2024-12-19 | 19:14 | 21.942 | 85.3873 | 26.31 | 76.97 | 17 | REST SHELTER | 0 | 3884
2024-12-19 | 19:14 | 21.942 | 85.3873 | 26.31 | 76.97 | 17 | REST SHELTER | 0 | 3885
2024-12-19 | 19:14 | 21.942 | 85.3873 | 26.31 | 76.97 | 17 | REST SHELTER | 0 | 3886
2024-12-19 | 19:14 | 21.942 | 85.3873 | 26.31 | 79.7 | 17 | REST SHELTER | 0 | 3887
2024-12-19 | 19:14 | 21.942 | 85.3873 | 26.31 | 79.7 | 17 | REST SHELTER | 0 | 3888
2024-12-19 | 19:14 | 21.942 | 85.3873 | 26.31 | 79.7 | 17 | REST SHELTER | 0 | 3889
2024-12-19 | 19:14 | 21.942 | 85.3873 | 26.31 | 76.97 | 17 | REST SHELTER | 0 | 3890
2024-12-19 | 19:14 | 21.942 | 85.3873 | 26.31 | 76.97 | 17 | REST SHELTER | 0 | 3891
2024-12-19 | 19:14 | 21.942 | 85.3873 | 26.31 | 76.97 | 17 | REST SHELTER | 0 | 3892
2024-12-19 | 19:14 | 21.942 | 85.3873 | 26.31 | 76.97 | 17 | REST SHELTER | 0 | 3893
2024-12-19 | 19:14 | 21.942 | 85.3873 | 26.31 | 76.97 | 17 | REST SHELTER | 0 | 3894
2024-12-19 | 19:14 | 21.942 | 85.3873 | 26.31 | 79.7 | 17 | REST SHELTER | 0 | 3895
2024-12-19 | 19:14 | 21.942 | 85.3873 | 30.73 | 87.87 | 17 | REST SHELTER | 0 | 3896
2024-12-19 | 19:15 | 21.942 | 85.3874 | 26.31 | 90.59 | 17 | REST SHELTER | 10.3139 | 3897
2024-12-19 | 19:15 | 21.942 | 85.3874 | 52.48 | 131.52 | 17 | REST SHELTER | 0 | 3898
2024-12-19 | 19:15 | 21.942 | 85.3874 | 120.6 | 180.75 | 17 | REST SHELTER | 0 | 3899
2024-12-19 | 19:15 | 21.942 | 85.3874 | 249.35 | 139.72 | 17 | REST SHELTER | 0 | 3900
2024-12-19 | 19:15 | 21.9421 | 85.3874 | 232.86 | 117.87 | 6 | HAUL ROAD | 11.12 | 3901
2024-12-19 | 19:15 | 21.9421 | 85.3874 | 134.25 | 71.53 | 6 | HAUL ROAD | 0.094935 | 3902
2024-12-19 | 19:15 | 21.9422 | 85.3874 | 60.64 | 12.8 | 6 | HAUL ROAD | 11.1196 | 3903
2024-12-19 | 19:15 | 21.9422 | 85.3874 | 7.58 | 21.12 | 6 | HAUL ROAD | 0 | 3904
2024-12-19 | 19:15 | 21.9423 | 85.3874 | 23.79 | 38.88 | 6 | HAUL ROAD | 11.1192 | 3905
2024-12-19 | 19:15 | 21.9423 | 85.3873 | 57.92 | 21.12 | 6 | HAUL ROAD | 10.3135 | 3906
2024-12-19 | 19:15 | 21.9423 | 85.3872 | 52.48 | 7.58 | 6 | HAUL ROAD | 10.3135 | 3907
2024-12-19 | 19:15 | 21.9423 | 85.3872 | 23.79 | 10.12 | 6 | HAUL ROAD | 0 | 3908
2024-12-19 | 19:15 | 21.9424 | 85.3871 | 3.16 | 10.12 | 6 | HAUL ROAD | 15.1662 | 3909
2024-12-19 | 19:15 | 21.9424 | 85.3871 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 3910
2024-12-19 | 19:15 | 21.9424 | 85.3871 | 0 | 18.36 | 6 | HAUL ROAD | 0 | 3911
2024-12-19 | 19:15 | 21.9424 | 85.387 | 5.24 | 21.12 | 6 | HAUL ROAD | 10.3139 | 3912
2024-12-19 | 19:15 | 21.9424 | 85.387 | 3.16 | 26.31 | 6 | HAUL ROAD | 0 | 3913
2024-12-19 | 19:15 | 21.9424 | 85.3869 | 5.24 | 26.31 | 6 | HAUL ROAD | 10.3139 | 3914
2024-12-19 | 19:15 | 21.9424 | 85.3869 | 10.12 | 36.16 | 6 | HAUL ROAD | 0 | 3915
2024-12-19 | 19:15 | 21.9425 | 85.3868 | 18.36 | 44.32 | 6 | HAUL ROAD | 15.1665 | 3916
2024-12-19 | 19:15 | 21.9425 | 85.3868 | 41.6 | 55.2 | 6 | HAUL ROAD | 0 | 3917
2024-12-19 | 19:15 | 21.9425 | 85.3867 | 71.53 | 41.6 | 6 | HAUL ROAD | 10.3135 | 3918
2024-12-19 | 19:15 | 21.9425 | 85.3866 | 30.73 | 26.31 | 6 | HAUL ROAD | 10.3135 | 3919
2024-12-19 | 19:15 | 21.9425 | 85.3866 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 3920
2024-12-19 | 19:15 | 21.9425 | 85.3865 | 44.32 | 7.58 | 6 | HAUL ROAD | 10.3135 | 3921
2024-12-19 | 19:15 | 21.9425 | 85.3865 | 41.6 | 5.24 | 6 | HAUL ROAD | 0 | 3922
2024-12-19 | 19:15 | 21.9424 | 85.3865 | 23.79 | 5.24 | 6 | HAUL ROAD | 11.1196 | 3923
2024-12-19 | 19:15 | 21.9424 | 85.3864 | 10.12 | 5.24 | 6 | HAUL ROAD | 10.3139 | 3924
2024-12-19 | 19:15 | 21.9424 | 85.3863 | 5.24 | 10.12 | 6 | HAUL ROAD | 10.3139 | 3925
2024-12-19 | 19:16 | 21.9424 | 85.3862 | 3.16 | 15.57 | 6 | HAUL ROAD | 10.3139 | 3926
2024-12-19 | 19:16 | 21.9423 | 85.3862 | 10.12 | 3.16 | 6 | HAUL ROAD | 11.1192 | 3927
2024-12-19 | 19:16 | 21.9423 | 85.3861 | 1.39 | 5.24 | 6 | HAUL ROAD | 10.3135 | 3928
2024-12-19 | 19:16 | 21.9423 | 85.386 | 10.12 | 0 | 6 | HAUL ROAD | 10.3135 | 3929
2024-12-19 | 19:16 | 21.9423 | 85.386 | 18.36 | 0 | 6 | HAUL ROAD | 0 | 3930
2024-12-19 | 19:16 | 21.9423 | 85.386 | 12.8 | 1.39 | 6 | HAUL ROAD | 0 | 3931
2024-12-19 | 19:16 | 21.9422 | 85.3859 | 15.57 | 3.16 | 6 | HAUL ROAD | 15.1662 | 3932
2024-12-19 | 19:16 | 21.9422 | 85.3859 | 12.8 | 3.16 | 6 | HAUL ROAD | 0 | 3933
2024-12-19 | 19:16 | 21.9422 | 85.3858 | 7.58 | 3.16 | 6 | HAUL ROAD | 10.3139 | 3934
2024-12-19 | 19:16 | 21.9422 | 85.3858 | 7.58 | 7.58 | 6 | HAUL ROAD | 0 | 3935
2024-12-19 | 19:16 | 21.9421 | 85.3857 | 7.58 | 10.12 | 6 | HAUL ROAD | 15.1665 | 3936
2024-12-19 | 19:16 | 21.9421 | 85.3856 | 21.12 | 15.57 | 6 | HAUL ROAD | 10.3144 | 3937
2024-12-19 | 19:16 | 21.942 | 85.3855 | 49.76 | 26.31 | 6 | HAUL ROAD | 15.1665 | 3938
2024-12-19 | 19:16 | 21.942 | 85.3855 | 21.12 | 5.24 | 6 | HAUL ROAD | 0 | 3939
2024-12-19 | 19:16 | 21.942 | 85.3854 | 7.58 | 7.58 | 6 | HAUL ROAD | 10.3139 | 3940
2024-12-19 | 19:16 | 21.942 | 85.3853 | 3.16 | 1.39 | 6 | HAUL ROAD | 10.3139 | 3941
2024-12-19 | 19:16 | 21.942 | 85.3852 | 1.39 | 0 | 6 | HAUL ROAD | 10.3139 | 3942
2024-12-19 | 19:16 | 21.9421 | 85.3852 | 3.16 | 3.16 | 6 | HAUL ROAD | 11.12 | 3943
2024-12-19 | 19:16 | 21.9421 | 85.3851 | 7.58 | 5.24 | 6 | HAUL ROAD | 10.3144 | 3944
2024-12-19 | 19:16 | 21.9421 | 85.3851 | 3.16 | 1.39 | 6 | HAUL ROAD | 0.094935 | 3945
2024-12-19 | 19:16 | 21.9421 | 85.3851 | 3.16 | 0 | 6 | HAUL ROAD | 0.094935 | 3946
2024-12-19 | 19:16 | 21.9421 | 85.385 | 0 | 3.16 | 6 | HAUL ROAD | 10.3144 | 3947
2024-12-19 | 19:16 | 21.9422 | 85.385 | 3.16 | 3.16 | 6 | HAUL ROAD | 11.1196 | 3948
2024-12-19 | 19:16 | 21.9422 | 85.3849 | 3.16 | 10.12 | 6 | HAUL ROAD | 10.3139 | 3949
2024-12-19 | 19:16 | 21.9423 | 85.3849 | 5.24 | 12.8 | 6 | HAUL ROAD | 11.1192 | 3950
2024-12-19 | 19:16 | 21.9423 | 85.3849 | 15.57 | 15.57 | 6 | HAUL ROAD | 0 | 3951
2024-12-19 | 19:16 | 21.9423 | 85.3849 | 15.57 | 21.12 | 6 | HAUL ROAD | 0 | 3952
2024-12-19 | 19:16 | 21.9424 | 85.385 | 18.36 | 26.31 | 6 | HAUL ROAD | 15.1662 | 3953
2024-12-19 | 19:16 | 21.9424 | 85.385 | 10.12 | 7.58 | 6 | HAUL ROAD | 0 | 3954
2024-12-19 | 19:16 | 21.9424 | 85.3851 | 7.58 | 15.57 | 6 | HAUL ROAD | 10.3139 | 3955
2024-12-19 | 19:16 | 21.9425 | 85.3852 | 18.36 | 10.12 | 6 | HAUL ROAD | 15.1665 | 3956
2024-12-19 | 19:17 | 21.9425 | 85.3852 | 10.12 | 15.57 | 6 | HAUL ROAD | 0 | 3957
2024-12-19 | 19:17 | 21.9426 | 85.3852 | 1.39 | 30.73 | 6 | HAUL ROAD | 11.1192 | 3958
2024-12-19 | 19:17 | 21.9427 | 85.3852 | 10.12 | 128.79 | 6 | HAUL ROAD | 11.12 | 3959
2024-12-19 | 19:17 | 21.9427 | 85.3852 | 18.36 | 0 | 6 | HAUL ROAD | 0 | 3960
2024-12-19 | 19:17 | 21.9428 | 85.3852 | 5.24 | 1.39 | 6 | HAUL ROAD | 11.12 | 3961
2024-12-19 | 19:17 | 21.9428 | 85.3852 | 1.39 | 1.39 | 6 | HAUL ROAD | 0.094935 | 3962
2024-12-19 | 19:17 | 21.9429 | 85.3852 | 0 | 1.39 | 6 | HAUL ROAD | 11.12 | 3963
2024-12-19 | 19:17 | 21.943 | 85.3852 | 0 | 3.16 | 6 | HAUL ROAD | 11.1196 | 3964
2024-12-19 | 19:17 | 21.9431 | 85.3852 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 3965
2024-12-19 | 19:17 | 21.9432 | 85.3852 | 10.12 | 7.58 | 6 | HAUL ROAD | 11.1192 | 3966
2024-12-19 | 19:17 | 21.9433 | 85.3852 | 5.24 | 18.36 | 6 | HAUL ROAD | 11.1192 | 3967
2024-12-19 | 19:17 | 21.9433 | 85.3851 | 23.79 | 10.12 | 6 | HAUL ROAD | 10.3139 | 3968
2024-12-19 | 19:17 | 21.9434 | 85.3851 | 3.16 | 5.24 | 6 | HAUL ROAD | 11.1192 | 3969
2024-12-19 | 19:17 | 21.9435 | 85.385 | 7.58 | 26.31 | 6 | HAUL ROAD | 15.1662 | 3970
2024-12-19 | 19:17 | 21.9436 | 85.385 | 12.8 | 3.16 | 6 | HAUL ROAD | 11.1192 | 3971
2024-12-19 | 19:17 | 21.9436 | 85.3849 | 0 | 5.24 | 6 | HAUL ROAD | 10.3139 | 3972
2024-12-19 | 19:17 | 21.9437 | 85.3848 | 0 | 10.12 | 6 | HAUL ROAD | 15.1662 | 3973
2024-12-19 | 19:17 | 21.9437 | 85.3848 | 7.58 | 18.36 | 6 | HAUL ROAD | 0 | 3974
2024-12-19 | 19:17 | 21.9437 | 85.3847 | 10.12 | 21.12 | 6 | HAUL ROAD | 10.3139 | 3975
2024-12-19 | 19:17 | 21.9438 | 85.3847 | 15.57 | 21.12 | 6 | HAUL ROAD | 11.1196 | 3976
2024-12-19 | 19:17 | 21.9438 | 85.3847 | 23.79 | 21.12 | 6 | HAUL ROAD | 0.094935 | 3977
2024-12-19 | 19:17 | 21.9439 | 85.3847 | 33.45 | 18.36 | 6 | HAUL ROAD | 11.1196 | 3978
2024-12-19 | 19:17 | 21.9439 | 85.3846 | 33.45 | 12.8 | 6 | HAUL ROAD | 10.3135 | 3979
2024-12-19 | 19:17 | 21.944 | 85.3846 | 47.04 | 10.12 | 6 | HAUL ROAD | 11.1192 | 3980
2024-12-19 | 19:17 | 21.9441 | 85.3846 | 71.53 | 26.31 | 6 | HAUL ROAD | 11.1196 | 3981
2024-12-19 | 19:17 | 21.9441 | 85.3847 | 82.42 | 30.73 | 6 | HAUL ROAD | 10.3135 | 3982
2024-12-19 | 19:17 | 21.9442 | 85.3847 | 68.8 | 44.32 | 6 | HAUL ROAD | 11.1192 | 3983
2024-12-19 | 19:17 | 21.9442 | 85.3847 | 57.92 | 30.73 | 6 | HAUL ROAD | 0 | 3984
2024-12-19 | 19:17 | 21.9443 | 85.3847 | 49.76 | 33.45 | 6 | HAUL ROAD | 11.12 | 3985
2024-12-19 | 19:18 | 21.9443 | 85.3847 | 38.88 | 36.16 | 6 | HAUL ROAD | 0.094935 | 3986
2024-12-19 | 19:18 | 21.9444 | 85.3847 | 30.73 | 26.31 | 6 | HAUL ROAD | 11.1196 | 3987
2024-12-19 | 19:18 | 21.9445 | 85.3848 | 26.31 | 26.31 | 6 | HAUL ROAD | 15.1662 | 3988
2024-12-19 | 19:18 | 21.9446 | 85.3848 | 15.57 | 10.12 | 6 | HAUL ROAD | 11.1196 | 3989
2024-12-19 | 19:18 | 21.9447 | 85.3848 | 1.39 | 10.12 | 6 | HAUL ROAD | 11.1192 | 3990
2024-12-19 | 19:18 | 21.9448 | 85.3848 | 5.24 | 10.12 | 6 | HAUL ROAD | 11.1196 | 3991
2024-12-19 | 19:18 | 21.9449 | 85.3848 | 12.8 | 12.8 | 6 | HAUL ROAD | 11.1196 | 3992
2024-12-19 | 19:18 | 21.945 | 85.3848 | 26.31 | 21.12 | 6 | HAUL ROAD | 11.1196 | 3993
2024-12-19 | 19:18 | 21.9452 | 85.3848 | 55.2 | 7.58 | 6 | HAUL ROAD | 22.2388 | 3994
2024-12-19 | 19:18 | 21.9453 | 85.3848 | 49.76 | 10.12 | 6 | HAUL ROAD | 11.1192 | 3995
2024-12-19 | 19:18 | 21.9454 | 85.3848 | 30.73 | 10.12 | 6 | HAUL ROAD | 11.1196 | 3996
2024-12-19 | 19:18 | 21.9455 | 85.3848 | 26.31 | 0 | 6 | HAUL ROAD | 11.1196 | 3997
2024-12-19 | 19:18 | 21.9457 | 85.3848 | 21.12 | 1.39 | 6 | HAUL ROAD | 22.2388 | 3998
2024-12-19 | 19:18 | 21.9458 | 85.3848 | 23.79 | 15.57 | 6 | HAUL ROAD | 11.1192 | 3999
2024-12-19 | 19:18 | 21.9459 | 85.3849 | 23.79 | 5.24 | 6 | HAUL ROAD | 15.1665 | 4000
2024-12-19 | 19:18 | 21.946 | 85.3849 | 30.73 | 7.58 | 6 | HAUL ROAD | 11.1196 | 4001
2024-12-19 | 19:18 | 21.9461 | 85.3849 | 15.57 | 7.58 | 6 | HAUL ROAD | 11.1196 | 4002
2024-12-19 | 19:18 | 21.9463 | 85.385 | 23.79 | 10.12 | 6 | HAUL ROAD | 24.5143 | 4003
2024-12-19 | 19:18 | 21.9464 | 85.385 | 66.08 | 33.45 | 6 | HAUL ROAD | 11.1196 | 4004
2024-12-19 | 19:18 | 21.9465 | 85.385 | 60.64 | 26.31 | 6 | HAUL ROAD | 11.1196 | 4005
2024-12-19 | 19:18 | 21.9466 | 85.3851 | 104.23 | 1.39 | 6 | HAUL ROAD | 15.1665 | 4006
2024-12-19 | 19:18 | 21.9467 | 85.3851 | 85.14 | 41.6 | 6 | HAUL ROAD | 11.1196 | 4007
2024-12-19 | 19:18 | 21.9468 | 85.3852 | 74.25 | 36.16 | 6 | HAUL ROAD | 15.1665 | 4008
2024-12-19 | 19:18 | 21.9469 | 85.3852 | 93.32 | 12.8 | 6 | HAUL ROAD | 11.1196 | 4009
2024-12-19 | 19:18 | 21.9471 | 85.3853 | 79.7 | 33.45 | 6 | HAUL ROAD | 24.5143 | 4010
2024-12-19 | 19:18 | 21.9472 | 85.3853 | 52.48 | 15.57 | 6 | HAUL ROAD | 11.1192 | 4011
2024-12-19 | 19:18 | 21.9472 | 85.3854 | 82.42 | 15.57 | 6 | HAUL ROAD | 10.3139 | 4012
2024-12-19 | 19:18 | 21.9473 | 85.3855 | 66.08 | 23.79 | 6 | HAUL ROAD | 15.1665 | 4013
2024-12-19 | 19:18 | 21.9473 | 85.3856 | 82.42 | 3.16 | 6 | HAUL ROAD | 10.3144 | 4014
2024-12-19 | 19:18 | 21.9472 | 85.3858 | 44.32 | 26.31 | 6 | HAUL ROAD | 23.4334 | 4015
2024-12-19 | 19:18 | 21.9472 | 85.3859 | 71.53 | 3.16 | 6 | HAUL ROAD | 10.3139 | 4016
2024-12-19 | 19:19 | 21.9472 | 85.386 | 63.36 | 18.36 | 6 | HAUL ROAD | 10.3139 | 4017
2024-12-19 | 19:19 | 21.9471 | 85.3861 | 63.36 | 26.31 | 6 | HAUL ROAD | 15.1665 | 4018
2024-12-19 | 19:19 | 21.9471 | 85.3862 | 55.2 | 3.16 | 6 | HAUL ROAD | 10.3139 | 4019
2024-12-19 | 19:19 | 21.947 | 85.3864 | 26.31 | 3.16 | 6 | HAUL ROAD | 23.4336 | 4020
2024-12-19 | 19:19 | 21.947 | 85.3865 | 3.16 | 3.16 | 6 | HAUL ROAD | 10.3144 | 4021
2024-12-19 | 19:19 | 21.947 | 85.3866 | 1.39 | 3.16 | 6 | HAUL ROAD | 10.3144 | 4022
2024-12-19 | 19:19 | 21.9469 | 85.3867 | 3.16 | 3.16 | 6 | HAUL ROAD | 15.1665 | 4023
2024-12-19 | 19:19 | 21.9469 | 85.3867 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 4024
2024-12-19 | 19:19 | 21.9469 | 85.3868 | 0 | 1.39 | 6 | HAUL ROAD | 10.3139 | 4025
2024-12-19 | 19:19 | 21.9469 | 85.3869 | 0 | 3.16 | 6 | HAUL ROAD | 10.3139 | 4026
2024-12-19 | 19:19 | 21.947 | 85.3869 | 26.31 | 0 | 6 | HAUL ROAD | 11.1192 | 4027
2024-12-19 | 19:19 | 21.9471 | 85.387 | 21.12 | 1.39 | 6 | HAUL ROAD | 15.1665 | 4028
2024-12-19 | 19:19 | 21.9471 | 85.387 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 4029
2024-12-19 | 19:19 | 21.9472 | 85.387 | 23.79 | 12.8 | 6 | HAUL ROAD | 11.1192 | 4030
2024-12-19 | 19:19 | 21.9473 | 85.387 | 23.79 | 5.24 | 6 | HAUL ROAD | 11.1196 | 4031
2024-12-19 | 19:19 | 21.9474 | 85.3871 | 15.57 | 5.24 | 6 | HAUL ROAD | 15.1665 | 4032
2024-12-19 | 19:19 | 21.9475 | 85.3871 | 1.39 | 0 | 6 | HAUL ROAD | 11.1192 | 4033
2024-12-19 | 19:19 | 21.9476 | 85.3872 | 36.16 | 1.39 | 6 | HAUL ROAD | 15.1665 | 4034
2024-12-19 | 19:19 | 21.9477 | 85.3872 | 12.8 | 10.12 | 6 | HAUL ROAD | 11.1196 | 4035
2024-12-19 | 19:19 | 21.9478 | 85.3872 | 10.12 | 7.58 | 6 | HAUL ROAD | 11.12 | 4036
2024-12-19 | 19:19 | 21.9479 | 85.3872 | 18.36 | 3.16 | 6 | HAUL ROAD | 11.1196 | 4037
2024-12-19 | 19:19 | 21.948 | 85.3873 | 12.8 | 7.58 | 6 | HAUL ROAD | 15.1659 | 4038
2024-12-19 | 19:19 | 21.9482 | 85.3873 | 3.16 | 10.12 | 6 | HAUL ROAD | 22.239 | 4039
2024-12-19 | 19:19 | 21.9483 | 85.3873 | 15.57 | 5.24 | 6 | HAUL ROAD | 11.1192 | 4040
2024-12-19 | 19:19 | 21.9484 | 85.3873 | 18.36 | 0 | 6 | HAUL ROAD | 11.1196 | 4041
2024-12-19 | 19:19 | 21.9485 | 85.3874 | 1.39 | 0 | 6 | HAUL ROAD | 15.1659 | 4042
2024-12-19 | 19:19 | 21.9487 | 85.3874 | 0 | 3.16 | 6 | HAUL ROAD | 22.2392 | 4043
2024-12-19 | 19:19 | 21.9488 | 85.3874 | 10.12 | 0 | 6 | HAUL ROAD | 11.1196 | 4044
2024-12-19 | 19:19 | 21.9489 | 85.3874 | 3.16 | 3.16 | 6 | HAUL ROAD | 11.1192 | 4045
2024-12-19 | 19:20 | 21.949 | 85.3874 | 3.16 | 1.39 | 6 | HAUL ROAD | 11.1196 | 4046
2024-12-19 | 19:20 | 21.9491 | 85.3874 | 3.16 | 0 | 6 | HAUL ROAD | 11.1196 | 4047
2024-12-19 | 19:20 | 21.9492 | 85.3874 | 3.16 | 5.24 | 6 | HAUL ROAD | 11.1196 | 4048
2024-12-19 | 19:20 | 21.9494 | 85.3875 | 3.16 | 3.16 | 6 | HAUL ROAD | 24.5141 | 4049
2024-12-19 | 19:20 | 21.9495 | 85.3875 | 3.16 | 0 | 6 | HAUL ROAD | 11.1192 | 4050
2024-12-19 | 19:20 | 21.9496 | 85.3875 | 1.39 | 5.24 | 6 | HAUL ROAD | 11.1192 | 4051
2024-12-19 | 19:20 | 21.9496 | 85.3876 | 5.24 | 3.16 | 6 | HAUL ROAD | 10.3135 | 4052
2024-12-19 | 19:20 | 21.9497 | 85.3876 | 12.8 | 10.12 | 6 | HAUL ROAD | 11.1192 | 4053
2024-12-19 | 19:20 | 21.9498 | 85.3876 | 10.12 | 0 | 6 | HAUL ROAD | 11.1196 | 4054
2024-12-19 | 19:20 | 21.9499 | 85.3877 | 1.39 | 0 | 6 | HAUL ROAD | 15.1665 | 4055
2024-12-19 | 19:20 | 21.9499 | 85.3878 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4056
2024-12-19 | 19:20 | 21.95 | 85.3878 | 0 | 1.39 | 6 | HAUL ROAD | 11.1196 | 4057
2024-12-19 | 19:20 | 21.95 | 85.388 | 3.16 | 3.16 | 6 | HAUL ROAD | 20.6272 | 4058
2024-12-19 | 19:20 | 21.9501 | 85.3881 | 12.8 | 3.16 | 6 | HAUL ROAD | 15.1662 | 4059
2024-12-19 | 19:20 | 21.9501 | 85.3882 | 0 | 7.58 | 6 | HAUL ROAD | 10.3139 | 4060
2024-12-19 | 19:20 | 21.9501 | 85.3883 | 1.39 | 12.8 | 6 | HAUL ROAD | 10.3139 | 4061
2024-12-19 | 19:20 | 21.9501 | 85.3884 | 0 | 18.36 | 6 | HAUL ROAD | 10.3139 | 4062
2024-12-19 | 19:20 | 21.9501 | 85.3885 | 0 | 10.12 | 6 | HAUL ROAD | 10.3139 | 4063
2024-12-19 | 19:20 | 21.9501 | 85.3887 | 0 | 5.24 | 6 | HAUL ROAD | 20.6272 | 4064
2024-12-19 | 19:20 | 21.9502 | 85.3888 | 0 | 3.16 | 6 | HAUL ROAD | 15.1662 | 4065
2024-12-19 | 19:20 | 21.9502 | 85.3889 | 3.16 | 10.12 | 6 | HAUL ROAD | 10.3139 | 4066
2024-12-19 | 19:20 | 21.9503 | 85.389 | 15.57 | 7.58 | 6 | HAUL ROAD | 15.1662 | 4067
2024-12-19 | 19:20 | 21.9504 | 85.3891 | 23.79 | 0 | 6 | HAUL ROAD | 15.1662 | 4068
2024-12-19 | 19:20 | 21.9504 | 85.3892 | 10.12 | 0 | 6 | HAUL ROAD | 10.3135 | 4069
2024-12-19 | 19:20 | 21.9505 | 85.3893 | 1.39 | 3.16 | 6 | HAUL ROAD | 15.1659 | 4070
2024-12-19 | 19:20 | 21.9506 | 85.3894 | 10.12 | 1.39 | 6 | HAUL ROAD | 15.1659 | 4071
2024-12-19 | 19:20 | 21.9507 | 85.3894 | 7.58 | 0 | 6 | HAUL ROAD | 11.1192 | 4072
2024-12-19 | 19:20 | 21.9508 | 85.3895 | 1.39 | 0 | 6 | HAUL ROAD | 15.1662 | 4073
2024-12-19 | 19:20 | 21.9509 | 85.3895 | 1.39 | 15.57 | 6 | HAUL ROAD | 11.1192 | 4074
2024-12-19 | 19:20 | 21.9511 | 85.3896 | 26.31 | 5.24 | 6 | HAUL ROAD | 24.5141 | 4075
2024-12-19 | 19:20 | 21.9512 | 85.3896 | 26.31 | 3.16 | 6 | HAUL ROAD | 11.1196 | 4076
2024-12-19 | 19:21 | 21.9513 | 85.3896 | 5.24 | 18.36 | 6 | HAUL ROAD | 11.1192 | 4077
2024-12-19 | 19:21 | 21.9514 | 85.3897 | 7.58 | 3.16 | 6 | HAUL ROAD | 15.1662 | 4078
2024-12-19 | 19:21 | 21.9515 | 85.3897 | 18.36 | 18.36 | 6 | HAUL ROAD | 11.1196 | 4079
2024-12-19 | 19:21 | 21.9517 | 85.3897 | 3.16 | 3.16 | 6 | HAUL ROAD | 22.239 | 4080
2024-12-19 | 19:21 | 21.9518 | 85.3897 | 60.64 | 1.39 | 6 | HAUL ROAD | 11.1196 | 4081
2024-12-19 | 19:21 | 21.9519 | 85.3897 | 21.12 | 26.31 | 6 | HAUL ROAD | 11.1192 | 4082
2024-12-19 | 19:21 | 21.952 | 85.3897 | 0 | 3.16 | 6 | HAUL ROAD | 11.1192 | 4083
2024-12-19 | 19:21 | 21.9522 | 85.3898 | 0 | 0 | 6 | HAUL ROAD | 24.5141 | 4084
2024-12-19 | 19:21 | 21.9523 | 85.3898 | 3.16 | 7.58 | 6 | HAUL ROAD | 11.1192 | 4085
2024-12-19 | 19:21 | 21.9524 | 85.3898 | 5.24 | 1.39 | 6 | HAUL ROAD | 11.1192 | 4086
2024-12-19 | 19:21 | 21.9525 | 85.3899 | 5.24 | 0 | 6 | HAUL ROAD | 15.1662 | 4087
2024-12-19 | 19:21 | 21.9527 | 85.3899 | 0 | 0 | 6 | HAUL ROAD | 22.2388 | 4088
2024-12-19 | 19:21 | 21.9528 | 85.39 | 1.39 | 0 | 6 | HAUL ROAD | 15.1659 | 4089
2024-12-19 | 19:21 | 21.9529 | 85.39 | 3.16 | 1.39 | 6 | HAUL ROAD | 11.1192 | 4090
2024-12-19 | 19:21 | 21.953 | 85.39 | 5.24 | 0 | 6 | HAUL ROAD | 11.1192 | 4091
2024-12-19 | 19:21 | 21.9531 | 85.3901 | 7.58 | 0 | 6 | HAUL ROAD | 15.1662 | 4092
2024-12-19 | 19:21 | 21.9533 | 85.3901 | 12.8 | 0 | 6 | HAUL ROAD | 22.2392 | 4093
2024-12-19 | 19:21 | 21.9534 | 85.3902 | 7.58 | 0 | 6 | HAUL ROAD | 15.1662 | 4094
2024-12-19 | 19:21 | 21.9535 | 85.3902 | 12.8 | 5.24 | 6 | HAUL ROAD | 11.1192 | 4095
2024-12-19 | 19:21 | 21.9536 | 85.3903 | 12.8 | 0 | 6 | HAUL ROAD | 15.1659 | 4096
2024-12-19 | 19:21 | 21.9537 | 85.3903 | 7.58 | 0 | 6 | HAUL ROAD | 11.1196 | 4097
2024-12-19 | 19:21 | 21.9538 | 85.3904 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4098
2024-12-19 | 19:21 | 21.9539 | 85.3904 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4099
2024-12-19 | 19:21 | 21.954 | 85.3905 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4100
2024-12-19 | 19:21 | 21.9542 | 85.3905 | 0 | 0 | 6 | HAUL ROAD | 22.239 | 4101
2024-12-19 | 19:21 | 21.9543 | 85.3906 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4102
2024-12-19 | 19:21 | 21.9544 | 85.3906 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4103
2024-12-19 | 19:21 | 21.9545 | 85.3907 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4104
2024-12-19 | 19:21 | 21.9546 | 85.3907 | 0 | 1.39 | 6 | HAUL ROAD | 11.12 | 4105
2024-12-19 | 19:22 | 21.9547 | 85.3908 | 1.39 | 7.58 | 6 | HAUL ROAD | 15.1659 | 4106
2024-12-19 | 19:22 | 21.9549 | 85.3909 | 0 | 1.39 | 6 | HAUL ROAD | 24.5141 | 4107
2024-12-19 | 19:22 | 21.955 | 85.3909 | 12.8 | 0 | 6 | HAUL ROAD | 11.1196 | 4108
2024-12-19 | 19:22 | 21.9551 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4109
2024-12-19 | 19:22 | 21.9552 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 4110
2024-12-19 | 19:22 | 21.9553 | 85.3911 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4111
2024-12-19 | 19:22 | 21.9554 | 85.3911 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4112
2024-12-19 | 19:22 | 21.9555 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4113
2024-12-19 | 19:22 | 21.9557 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 22.239 | 4114
2024-12-19 | 19:22 | 21.9558 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4115
2024-12-19 | 19:22 | 21.9559 | 85.3913 | 0 | 1.39 | 6 | HAUL ROAD | 11.1192 | 4116
2024-12-19 | 19:22 | 21.956 | 85.3914 | 0 | 3.16 | 6 | HAUL ROAD | 15.1659 | 4117
2024-12-19 | 19:22 | 21.9561 | 85.3915 | 0 | 3.16 | 6 | HAUL ROAD | 15.1659 | 4118
2024-12-19 | 19:22 | 21.9562 | 85.3915 | 10.12 | 5.24 | 6 | HAUL ROAD | 11.1192 | 4119
2024-12-19 | 19:22 | 21.9563 | 85.3916 | 18.36 | 0 | 6 | HAUL ROAD | 15.1659 | 4120
2024-12-19 | 19:22 | 21.9564 | 85.3916 | 3.16 | 0 | 6 | HAUL ROAD | 11.12 | 4121
2024-12-19 | 19:22 | 21.9566 | 85.3917 | 0 | 1.39 | 6 | HAUL ROAD | 24.5139 | 4122
2024-12-19 | 19:22 | 21.9567 | 85.3917 | 3.16 | 3.16 | 6 | HAUL ROAD | 11.1192 | 4123
2024-12-19 | 19:22 | 21.9568 | 85.3917 | 5.24 | 0 | 6 | HAUL ROAD | 11.12 | 4124
2024-12-19 | 19:22 | 21.9569 | 85.3918 | 7.58 | 0 | 6 | HAUL ROAD | 15.1662 | 4125
2024-12-19 | 19:22 | 21.957 | 85.3918 | 7.58 | 1.39 | 6 | HAUL ROAD | 11.12 | 4126
2024-12-19 | 19:22 | 21.9571 | 85.3918 | 12.8 | 3.16 | 6 | HAUL ROAD | 11.12 | 4127
2024-12-19 | 19:22 | 21.9572 | 85.3919 | 15.57 | 5.24 | 6 | HAUL ROAD | 15.1659 | 4128
2024-12-19 | 19:22 | 21.9574 | 85.3919 | 3.16 | 10.12 | 6 | HAUL ROAD | 22.239 | 4129
2024-12-19 | 19:22 | 21.9575 | 85.3919 | 1.39 | 0 | 6 | HAUL ROAD | 11.1196 | 4130
2024-12-19 | 19:22 | 21.9576 | 85.3919 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4131
2024-12-19 | 19:22 | 21.9576 | 85.3918 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 4132
2024-12-19 | 19:22 | 21.9577 | 85.3917 | 0 | 1.39 | 6 | HAUL ROAD | 15.1659 | 4133
2024-12-19 | 19:22 | 21.9577 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 4134
2024-12-19 | 19:22 | 21.9577 | 85.3915 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 4135
2024-12-19 | 19:22 | 21.9577 | 85.3915 | 0 | 0 | 6 | HAUL ROAD | 0 | 4136
2024-12-19 | 19:23 | 21.9577 | 85.3915 | 0 | 0 | 6 | HAUL ROAD | 0 | 4137
2024-12-19 | 19:23 | 21.9577 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 4138
2024-12-19 | 19:23 | 21.9577 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 4139
2024-12-19 | 19:23 | 21.9577 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4140
2024-12-19 | 19:23 | 21.9577 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 4141
2024-12-19 | 19:23 | 21.9577 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 0 | 4142
2024-12-19 | 19:23 | 21.9577 | 85.3911 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 4143
2024-12-19 | 19:23 | 21.9578 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 15.1662 | 4144
2024-12-19 | 19:23 | 21.9578 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4145
2024-12-19 | 19:23 | 21.9578 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4146
2024-12-19 | 19:23 | 21.9579 | 85.3909 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4147
2024-12-19 | 19:23 | 21.958 | 85.3909 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4148
2024-12-19 | 19:23 | 21.958 | 85.3909 | 0 | 0 | 6 | HAUL ROAD | 0 | 4149
2024-12-19 | 19:23 | 21.9581 | 85.3909 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4150
2024-12-19 | 19:23 | 21.9582 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4151
2024-12-19 | 19:23 | 21.9583 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4152
2024-12-19 | 19:23 | 21.9583 | 85.3911 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 4153
2024-12-19 | 19:23 | 21.9584 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4154
2024-12-19 | 19:23 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4155
2024-12-19 | 19:23 | 21.9584 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4156
2024-12-19 | 19:23 | 21.9584 | 85.3915 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4157
2024-12-19 | 19:23 | 21.9585 | 85.3915 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4158
2024-12-19 | 19:23 | 21.9585 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4159
2024-12-19 | 19:23 | 21.9585 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4160
2024-12-19 | 19:23 | 21.9585 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4161
2024-12-19 | 19:23 | 21.9585 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4162
2024-12-19 | 19:23 | 21.9585 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4163
2024-12-19 | 19:23 | 21.9585 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4164
2024-12-19 | 19:23 | 21.9585 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4165
2024-12-19 | 19:24 | 21.9585 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4166
2024-12-19 | 19:24 | 21.9585 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4167
2024-12-19 | 19:24 | 21.9585 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4168
2024-12-19 | 19:24 | 21.9585 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4169
2024-12-19 | 19:24 | 21.9585 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4170
2024-12-19 | 19:24 | 21.9585 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4171
2024-12-19 | 19:24 | 21.9585 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 0 | 4172
2024-12-19 | 19:24 | 21.9585 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 0 | 4173
2024-12-19 | 19:24 | 21.9585 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 0 | 4174
2024-12-19 | 19:24 | 21.9585 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 0 | 4175
2024-12-19 | 19:24 | 21.9585 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 0 | 4176
2024-12-19 | 19:24 | 21.9585 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 0 | 4177
2024-12-19 | 19:24 | 21.9585 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 0 | 4178
2024-12-19 | 19:24 | 21.9585 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 0 | 4179
2024-12-19 | 19:24 | 21.9585 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 0 | 4180
2024-12-19 | 19:24 | 21.9585 | 85.3918 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4181
2024-12-19 | 19:24 | 21.9586 | 85.3918 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4182
2024-12-19 | 19:24 | 21.9586 | 85.3918 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4183
2024-12-19 | 19:24 | 21.9586 | 85.3918 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4184
2024-12-19 | 19:24 | 21.9586 | 85.3918 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4185
2024-12-19 | 19:24 | 21.9586 | 85.3919 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4186
2024-12-19 | 19:24 | 21.9586 | 85.3919 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4187
2024-12-19 | 19:24 | 21.9586 | 85.3919 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4188
2024-12-19 | 19:24 | 21.9585 | 85.392 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4189
2024-12-19 | 19:24 | 21.9585 | 85.3919 | 0 | 1.39 | 6 | HAUL ROAD | 10.3135 | 4190
2024-12-19 | 19:24 | 21.9585 | 85.3919 | 0 | 7.58 | 6 | HAUL ROAD | 0 | 4191
2024-12-19 | 19:24 | 21.9585 | 85.3919 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 4192
2024-12-19 | 19:24 | 21.9585 | 85.3919 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 4193
2024-12-19 | 19:24 | 21.9585 | 85.3919 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 4194
2024-12-19 | 19:24 | 21.9585 | 85.3918 | 0 | 3.16 | 6 | HAUL ROAD | 10.3135 | 4195
2024-12-19 | 19:24 | 21.9585 | 85.3918 | 0 | 0 | 6 | HAUL ROAD | 0 | 4196
2024-12-19 | 19:25 | 21.9585 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4197
2024-12-19 | 19:25 | 21.9585 | 85.3916 | 0 | 1.39 | 6 | HAUL ROAD | 10.3135 | 4198
2024-12-19 | 19:25 | 21.9585 | 85.3915 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4199
2024-12-19 | 19:25 | 21.9585 | 85.3915 | 0 | 0 | 6 | HAUL ROAD | 0 | 4200
2024-12-19 | 19:25 | 21.9584 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4201
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4202
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4203
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4204
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4205
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4206
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4207
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4208
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4209
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4210
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4211
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4212
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4213
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4214
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4215
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4216
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4217
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4218
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4219
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4220
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4221
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4222
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4223
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4224
2024-12-19 | 19:25 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4225
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4226
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4227
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4228
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4229
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4230
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4231
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4232
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4233
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4234
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4235
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4236
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4237
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4238
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4239
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4240
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4241
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4242
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4243
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4244
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4245
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4246
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4247
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4248
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4249
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4250
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4251
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4252
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4253
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4254
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4255
2024-12-19 | 19:26 | 21.9584 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4256
2024-12-19 | 19:27 | 21.9584 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4257
2024-12-19 | 19:27 | 21.9584 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 0 | 4258
2024-12-19 | 19:27 | 21.9583 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4259
2024-12-19 | 19:27 | 21.9583 | 85.3911 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 4260
2024-12-19 | 19:27 | 21.9582 | 85.3911 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4261
2024-12-19 | 19:27 | 21.9582 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4262
2024-12-19 | 19:27 | 21.9581 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4263
2024-12-19 | 19:27 | 21.958 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4264
2024-12-19 | 19:27 | 21.9579 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4265
2024-12-19 | 19:27 | 21.9579 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0 | 4266
2024-12-19 | 19:27 | 21.9578 | 85.3911 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4267
2024-12-19 | 19:27 | 21.9578 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4268
2024-12-19 | 19:27 | 21.9577 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 4269
2024-12-19 | 19:27 | 21.9577 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 4270
2024-12-19 | 19:27 | 21.9577 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 4271
2024-12-19 | 19:27 | 21.9577 | 85.3915 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 4272
2024-12-19 | 19:27 | 21.9577 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 4273
2024-12-19 | 19:27 | 21.9577 | 85.3917 | 0 | 1.39 | 6 | HAUL ROAD | 10.313 | 4274
2024-12-19 | 19:27 | 21.9577 | 85.3918 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 4275
2024-12-19 | 19:27 | 21.9577 | 85.3919 | 0 | 3.16 | 6 | HAUL ROAD | 10.313 | 4276
2024-12-19 | 19:27 | 21.9576 | 85.3919 | 0 | 10.12 | 6 | HAUL ROAD | 11.1196 | 4277
2024-12-19 | 19:27 | 21.9575 | 85.3919 | 0 | 15.57 | 6 | HAUL ROAD | 11.1196 | 4278
2024-12-19 | 19:27 | 21.9574 | 85.3919 | 5.24 | 1.39 | 6 | HAUL ROAD | 11.1196 | 4279
2024-12-19 | 19:27 | 21.9573 | 85.3919 | 3.16 | 5.24 | 6 | HAUL ROAD | 11.1192 | 4280
2024-12-19 | 19:27 | 21.9572 | 85.3919 | 7.58 | 1.39 | 6 | HAUL ROAD | 11.1196 | 4281
2024-12-19 | 19:27 | 21.9571 | 85.3919 | 7.58 | 1.39 | 6 | HAUL ROAD | 11.1196 | 4282
2024-12-19 | 19:27 | 21.957 | 85.3918 | 21.12 | 3.16 | 6 | HAUL ROAD | 15.1659 | 4283
2024-12-19 | 19:27 | 21.9569 | 85.3918 | 12.8 | 1.39 | 6 | HAUL ROAD | 11.12 | 4284
2024-12-19 | 19:27 | 21.9568 | 85.3918 | 7.58 | 0 | 6 | HAUL ROAD | 11.12 | 4285
2024-12-19 | 19:28 | 21.9567 | 85.3917 | 7.58 | 1.39 | 6 | HAUL ROAD | 15.1662 | 4286
2024-12-19 | 19:28 | 21.9566 | 85.3917 | 5.24 | 0 | 6 | HAUL ROAD | 11.1192 | 4287
2024-12-19 | 19:28 | 21.9565 | 85.3916 | 1.39 | 3.16 | 6 | HAUL ROAD | 15.1656 | 4288
2024-12-19 | 19:28 | 21.9564 | 85.3916 | 1.39 | 3.16 | 6 | HAUL ROAD | 11.1196 | 4289
2024-12-19 | 19:28 | 21.9563 | 85.3916 | 1.39 | 7.58 | 6 | HAUL ROAD | 11.12 | 4290
2024-12-19 | 19:28 | 21.9562 | 85.3915 | 15.57 | 10.12 | 6 | HAUL ROAD | 15.1659 | 4291
2024-12-19 | 19:28 | 21.9561 | 85.3915 | 26.31 | 0 | 6 | HAUL ROAD | 11.1192 | 4292
2024-12-19 | 19:28 | 21.956 | 85.3914 | 7.58 | 0 | 6 | HAUL ROAD | 15.1659 | 4293
2024-12-19 | 19:28 | 21.9559 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4294
2024-12-19 | 19:28 | 21.9558 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4295
2024-12-19 | 19:28 | 21.9557 | 85.3912 | 0 | 1.39 | 6 | HAUL ROAD | 15.1659 | 4296
2024-12-19 | 19:28 | 21.9556 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4297
2024-12-19 | 19:28 | 21.9555 | 85.3911 | 0 | 3.16 | 6 | HAUL ROAD | 15.1659 | 4298
2024-12-19 | 19:28 | 21.9554 | 85.3911 | 0 | 1.39 | 6 | HAUL ROAD | 11.1196 | 4299
2024-12-19 | 19:28 | 21.9553 | 85.391 | 0 | 3.16 | 6 | HAUL ROAD | 15.1659 | 4300
2024-12-19 | 19:28 | 21.9552 | 85.391 | 0 | 5.24 | 6 | HAUL ROAD | 11.1196 | 4301
2024-12-19 | 19:28 | 21.9551 | 85.3909 | 0 | 10.12 | 6 | HAUL ROAD | 15.1659 | 4302
2024-12-19 | 19:28 | 21.955 | 85.3909 | 3.16 | 15.57 | 6 | HAUL ROAD | 11.1196 | 4303
2024-12-19 | 19:28 | 21.9548 | 85.3908 | 5.24 | 15.57 | 6 | HAUL ROAD | 24.5139 | 4304
2024-12-19 | 19:28 | 21.9547 | 85.3908 | 74.25 | 36.16 | 6 | HAUL ROAD | 11.1192 | 4305
2024-12-19 | 19:28 | 21.9546 | 85.3907 | 76.97 | 0 | 6 | HAUL ROAD | 15.1659 | 4306
2024-12-19 | 19:28 | 21.9545 | 85.3907 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 4307
45645 | 0.81127 | 21.9544 | 85.3906 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4308
45645 | 0.8113 | 21.9543 | 85.3906 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4309
45645 | 0.81132 | 21.9542 | 85.3905 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4310
45645 | 0.81134 | 21.9541 | 85.3905 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4311
45645 | 0.81137 | 21.954 | 85.3904 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4312
45645 | 0.81139 | 21.9539 | 85.3904 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4313
45645 | 0.81141 | 21.9538 | 85.3903 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4314
45645 | 0.81144 | 21.9536 | 85.3903 | 0 | 1.39 | 6 | HAUL ROAD | 22.239 | 4315
45645 | 0.81146 | 21.9535 | 85.3902 | 7.58 | 0 | 6 | HAUL ROAD | 15.1659 | 4316
45645 | 0.81148 | 21.9534 | 85.3902 | 15.57 | 5.24 | 6 | HAUL ROAD | 11.1192 | 4317
45645 | 0.8115 | 21.9533 | 85.3901 | 15.57 | 1.39 | 6 | HAUL ROAD | 15.1662 | 4318
45645 | 0.81153 | 21.9532 | 85.3901 | 5.24 | 3.16 | 6 | HAUL ROAD | 11.1196 | 4319
45645 | 0.81155 | 21.9531 | 85.3901 | 12.8 | 3.16 | 6 | HAUL ROAD | 11.1196 | 4320
45645 | 0.81157 | 21.953 | 85.39 | 10.12 | 0 | 6 | HAUL ROAD | 15.1662 | 4321
45645 | 0.8116 | 21.9529 | 85.39 | 3.16 | 3.16 | 6 | HAUL ROAD | 11.1192 | 4322
45645 | 0.81162 | 21.9528 | 85.39 | 5.24 | 0 | 6 | HAUL ROAD | 11.1192 | 4323
45645 | 0.81164 | 21.9527 | 85.3899 | 1.39 | 0 | 6 | HAUL ROAD | 15.1659 | 4324
45645 | 0.81167 | 21.9526 | 85.3899 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4325
45645 | 0.81169 | 21.9525 | 85.3898 | 3.16 | 1.39 | 6 | HAUL ROAD | 15.1659 | 4326
45645 | 0.81171 | 21.9523 | 85.3898 | 1.39 | 3.16 | 6 | HAUL ROAD | 22.239 | 4327
45645 | 0.81174 | 21.9522 | 85.3898 | 3.16 | 1.39 | 6 | HAUL ROAD | 11.1192 | 4328
45645 | 0.81176 | 21.9521 | 85.3898 | 1.39 | 0 | 6 | HAUL ROAD | 11.1192 | 4329
45645 | 0.81178 | 21.952 | 85.3898 | 0 | 1.39 | 6 | HAUL ROAD | 11.1196 | 4330
45645 | 0.81181 | 21.9519 | 85.3897 | 0 | 3.16 | 6 | HAUL ROAD | 15.1659 | 4331
45645 | 0.81183 | 21.9518 | 85.3897 | 15.57 | 30.73 | 6 | HAUL ROAD | 11.1192 | 4332
45645 | 0.81185 | 21.9517 | 85.3897 | 5.24 | 18.36 | 6 | HAUL ROAD | 11.1196 | 4333
45645 | 0.81188 | 21.9516 | 85.3897 | 57.92 | 10.12 | 6 | HAUL ROAD | 11.12 | 4334
45645 | 0.8119 | 21.9515 | 85.3897 | 7.58 | 18.36 | 6 | HAUL ROAD | 11.1192 | 4335
45645 | 0.81192 | 21.9514 | 85.3897 | 18.36 | 5.24 | 6 | HAUL ROAD | 11.1196 | 4336
45645 | 0.81194 | 21.9513 | 85.3896 | 7.58 | 23.79 | 6 | HAUL ROAD | 15.1662 | 4337
45645 | 0.81197 | 21.9512 | 85.3896 | 10.12 | 12.8 | 6 | HAUL ROAD | 11.1192 | 4338
45645 | 0.81199 | 21.9511 | 85.3896 | 15.57 | 33.45 | 6 | HAUL ROAD | 11.1196 | 4339
45645 | 0.81201 | 21.951 | 85.3895 | 12.8 | 23.79 | 6 | HAUL ROAD | 15.1659 | 4340
45645 | 0.81204 | 21.9509 | 85.3895 | 21.12 | 5.24 | 6 | HAUL ROAD | 11.1196 | 4341
45645 | 0.81206 | 21.9508 | 85.3894 | 0 | 5.24 | 6 | HAUL ROAD | 15.1659 | 4342
45645 | 0.81208 | 21.9507 | 85.3894 | 0 | 12.8 | 6 | HAUL ROAD | 11.1196 | 4343
45645 | 0.81211 | 21.9506 | 85.3893 | 12.8 | 18.36 | 6 | HAUL ROAD | 15.1659 | 4344
45645 | 0.81213 | 21.9505 | 85.3893 | 12.8 | 12.8 | 6 | HAUL ROAD | 11.1192 | 4345
45645 | 0.81215 | 21.9504 | 85.3892 | 3.16 | 15.57 | 6 | HAUL ROAD | 15.1659 | 4346
45645 | 0.81218 | 21.9504 | 85.3892 | 10.12 | 15.57 | 6 | HAUL ROAD | 0 | 4347
45645 | 0.8122 | 21.9504 | 85.3891 | 18.36 | 5.24 | 6 | HAUL ROAD | 10.3135 | 4348
45645 | 0.81222 | 21.9504 | 85.389 | 12.8 | 0 | 6 | HAUL ROAD | 10.3135 | 4349
45645 | 0.81225 | 21.9505 | 85.389 | 3.16 | 0 | 6 | HAUL ROAD | 11.1192 | 4350
45645 | 0.81227 | 21.9505 | 85.389 | 0 | 0 | 6 | HAUL ROAD | 0 | 4351
45645 | 0.81229 | 21.9506 | 85.3891 | 1.39 | 0 | 6 | HAUL ROAD | 15.1659 | 4352
45645 | 0.81231 | 21.9507 | 85.3891 | 1.39 | 5.24 | 6 | HAUL ROAD | 11.1192 | 4353
45645 | 0.81234 | 21.9508 | 85.3892 | 0 | 3.16 | 6 | HAUL ROAD | 15.1662 | 4354
45645 | 0.81236 | 21.9508 | 85.3892 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 4355
45645 | 0.81238 | 21.9509 | 85.3893 | 0 | 5.24 | 6 | HAUL ROAD | 15.1659 | 4356
45645 | 0.81241 | 21.951 | 85.3893 | 1.39 | 10.12 | 6 | HAUL ROAD | 11.1196 | 4357
45645 | 0.81243 | 21.9511 | 85.3894 | 0 | 15.57 | 6 | HAUL ROAD | 15.1659 | 4358
45645 | 0.81245 | 21.9511 | 85.3894 | 1.39 | 12.8 | 6 | HAUL ROAD | 0 | 4359
45645 | 0.81248 | 21.9512 | 85.3894 | 3.16 | 3.16 | 6 | HAUL ROAD | 11.1196 | 4360
45645 | 0.8125 | 21.9513 | 85.3895 | 3.16 | 10.12 | 6 | HAUL ROAD | 15.1659 | 4361
45645 | 0.81252 | 21.9514 | 85.3895 | 7.58 | 1.39 | 6 | HAUL ROAD | 11.1196 | 4362
45645 | 0.81255 | 21.9515 | 85.3895 | 3.16 | 7.58 | 6 | HAUL ROAD | 11.1196 | 4363
45645 | 0.81257 | 21.9516 | 85.3895 | 12.8 | 5.24 | 6 | HAUL ROAD | 11.1192 | 4364
45645 | 0.81259 | 21.9517 | 85.3895 | 7.58 | 12.8 | 6 | HAUL ROAD | 11.12 | 4365
45645 | 0.81262 | 21.9518 | 85.3896 | 15.57 | 1.39 | 6 | HAUL ROAD | 15.1662 | 4366
45645 | 0.81264 | 21.9519 | 85.3896 | 3.16 | 12.8 | 6 | HAUL ROAD | 11.1192 | 4367
45645 | 0.81266 | 21.952 | 85.3896 | 21.12 | 15.57 | 6 | HAUL ROAD | 11.1192 | 4368
45645 | 0.81269 | 21.9521 | 85.3896 | 10.12 | 47.04 | 6 | HAUL ROAD | 11.1196 | 4369
45645 | 0.81271 | 21.9522 | 85.3896 | 178.02 | 145.18 | 6 | HAUL ROAD | 11.1192 | 4370
45645 | 0.81273 | 21.9523 | 85.3896 | 23.79 | 5.24 | 6 | HAUL ROAD | 11.1192 | 4371
45645 | 0.81275 | 21.9524 | 85.3896 | 38.88 | 10.12 | 6 | HAUL ROAD | 11.1192 | 4372
45645 | 0.81278 | 21.9525 | 85.3896 | 0 | 7.58 | 6 | HAUL ROAD | 11.1196 | 4373
45645 | 0.8128 | 21.9526 | 85.3896 | 33.45 | 3.16 | 6 | HAUL ROAD | 11.1192 | 4374
45645 | 0.81282 | 21.9527 | 85.3897 | 15.57 | 26.31 | 6 | HAUL ROAD | 15.1659 | 4375
45645 | 0.81285 | 21.9528 | 85.3897 | 33.45 | 3.16 | 6 | HAUL ROAD | 11.1192 | 4376
45645 | 0.81287 | 21.9529 | 85.3897 | 0 | 3.16 | 6 | HAUL ROAD | 11.1192 | 4377
45645 | 0.81289 | 21.9529 | 85.3898 | 1.39 | 10.12 | 6 | HAUL ROAD | 10.3135 | 4378
45645 | 0.81292 | 21.953 | 85.3898 | 10.12 | 12.8 | 6 | HAUL ROAD | 11.1192 | 4379
45645 | 0.81294 | 21.953 | 85.3899 | 12.8 | 1.39 | 6 | HAUL ROAD | 10.3135 | 4380
45645 | 0.81296 | 21.9531 | 85.3899 | 26.31 | 60.64 | 6 | HAUL ROAD | 11.1196 | 4381
45645 | 0.81299 | 21.9532 | 85.3899 | 76.97 | 0 | 6 | HAUL ROAD | 11.1196 | 4382
45645 | 0.81301 | 21.9533 | 85.3899 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4383
45645 | 0.81303 | 21.9534 | 85.39 | 0 | 0 | 6 | HAUL ROAD | 15.1662 | 4384
45645 | 0.81306 | 21.9535 | 85.39 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4385
45645 | 0.81308 | 21.9536 | 85.3901 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4386
45645 | 0.8131 | 21.9537 | 85.3901 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4387
45645 | 0.81312 | 21.9537 | 85.3901 | 0 | 0 | 6 | HAUL ROAD | 0 | 4388
45645 | 0.81315 | 21.9538 | 85.3901 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4389
45645 | 0.81317 | 21.9539 | 85.3902 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4390
45645 | 0.81319 | 21.954 | 85.3902 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4391
45645 | 0.81322 | 21.9541 | 85.3902 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4392
45645 | 0.81324 | 21.9541 | 85.3903 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 4393
45645 | 0.81326 | 21.9542 | 85.3903 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4394
45645 | 0.81329 | 21.9543 | 85.3903 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 4395
45645 | 0.81331 | 21.9543 | 85.3904 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4396
45645 | 0.81333 | 21.9544 | 85.3904 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4397
45645 | 0.81336 | 21.9545 | 85.3904 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 4398
45645 | 0.81338 | 21.9546 | 85.3905 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4399
45645 | 0.8134 | 21.9547 | 85.3905 | 0 | 3.16 | 6 | HAUL ROAD | 11.1196 | 4400
45645 | 0.81343 | 21.9548 | 85.3906 | 0 | 18.36 | 6 | HAUL ROAD | 15.1659 | 4401
45645 | 0.81345 | 21.9549 | 85.3906 | 0 | 44.32 | 6 | HAUL ROAD | 11.1196 | 4402
45645 | 0.81347 | 21.955 | 85.3907 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4403
45645 | 0.8135 | 21.9551 | 85.3907 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4404
45645 | 0.81352 | 21.9552 | 85.3908 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4405
45645 | 0.81354 | 21.9553 | 85.3908 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4406
45645 | 0.81356 | 21.9554 | 85.3909 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4407
45645 | 0.81359 | 21.9555 | 85.3909 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4408
45645 | 0.81361 | 21.9556 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4409
45645 | 0.81363 | 21.9557 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4410
45645 | 0.81366 | 21.9558 | 85.3911 | 0 | 1.39 | 6 | HAUL ROAD | 15.1659 | 4411
45645 | 0.81368 | 21.9559 | 85.3911 | 0 | 1.39 | 6 | HAUL ROAD | 11.1192 | 4412
45645 | 0.8137 | 21.956 | 85.3912 | 0 | 3.16 | 6 | HAUL ROAD | 15.1659 | 4413
45645 | 0.81373 | 21.9561 | 85.3912 | 0 | 10.12 | 6 | HAUL ROAD | 11.1192 | 4414
45645 | 0.81375 | 21.9562 | 85.3913 | 0 | 33.45 | 6 | HAUL ROAD | 15.1656 | 4415
45645 | 0.81377 | 21.9563 | 85.3913 | 0 | 52.48 | 6 | HAUL ROAD | 11.1196 | 4416
45645 | 0.8138 | 21.9564 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4417
45645 | 0.81382 | 21.9565 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4418
45645 | 0.81384 | 21.9566 | 85.3915 | 0 | 0 | 6 | HAUL ROAD | 15.1656 | 4419
45645 | 0.81387 | 21.9567 | 85.3915 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4420
45645 | 0.81389 | 21.9568 | 85.3915 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 4421
45645 | 0.81391 | 21.957 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 24.5141 | 4422
45645 | 0.81394 | 21.9571 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 4423
45645 | 0.81396 | 21.9572 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4424
45645 | 0.81398 | 21.9573 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4425
45645 | 0.814 | 21.9574 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4426
45645 | 0.81403 | 21.9575 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4427
45645 | 0.81405 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 4428
45645 | 0.81407 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4429
45645 | 0.8141 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4430
45645 | 0.81412 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4431
45645 | 0.81414 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4432
45645 | 0.81417 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4433
45645 | 0.81419 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4434
45645 | 0.81421 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4435
45645 | 0.81424 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4436
45645 | 0.81426 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4437
45645 | 0.81428 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4438
45645 | 0.81431 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4439
45645 | 0.81433 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4440
45645 | 0.81435 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4441
45645 | 0.81437 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4442
45645 | 0.8144 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4443
45645 | 0.81442 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4444
45645 | 0.81444 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4445
45645 | 0.81447 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4446
45645 | 0.81449 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4447
45645 | 0.81451 | 21.9575 | 85.3916 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 4448
45645 | 0.81454 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4449
45645 | 0.81456 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4450
45645 | 0.81458 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4451
45645 | 0.81461 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4452
45645 | 0.81463 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4453
45645 | 0.81465 | 21.9575 | 85.3915 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 4454
45645 | 0.81468 | 21.9575 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 4455
45645 | 0.8147 | 21.9575 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 4456
45645 | 0.81472 | 21.9575 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 4457
45645 | 0.81475 | 21.9575 | 85.3911 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 4458
45645 | 0.81477 | 21.9576 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4459
45645 | 0.81479 | 21.9576 | 85.3909 | 0 | 0 | 6 | HAUL ROAD | 10.313 | 4460
45645 | 0.81481 | 21.9577 | 85.3909 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4461
45645 | 0.81484 | 21.9578 | 85.3908 | 0 | 0 | 6 | HAUL ROAD | 15.1662 | 4462
45645 | 0.81486 | 21.9578 | 85.3907 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4463
45645 | 0.81488 | 21.9579 | 85.3907 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4464
45645 | 0.81491 | 21.958 | 85.3907 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4465
45645 | 0.81493 | 21.9581 | 85.3907 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4466
45645 | 0.81495 | 21.9582 | 85.3907 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4467
45645 | 0.81498 | 21.9583 | 85.3907 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4468
45645 | 0.815 | 21.9584 | 85.3907 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4469
45645 | 0.81502 | 21.9585 | 85.3908 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4470
45645 | 0.81505 | 21.9585 | 85.3908 | 0 | 0 | 6 | HAUL ROAD | 0 | 4471
45645 | 0.81507 | 21.9586 | 85.3909 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4472
45645 | 0.81509 | 21.9586 | 85.3909 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4473
45645 | 0.81512 | 21.9586 | 85.3909 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4474
45645 | 0.81514 | 21.9586 | 85.3909 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4475
45645 | 0.81516 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 15.1662 | 4476
45645 | 0.81519 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4477
45645 | 0.81521 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4478
45645 | 0.81523 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4479
45645 | 0.81525 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4480
45645 | 0.81528 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4481
45645 | 0.8153 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4482
45645 | 0.81532 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4483
45645 | 0.81535 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4484
45645 | 0.81537 | 21.9587 | 85.391 | 0 | 1.39 | 6 | HAUL ROAD | 0.094935 | 4485
45645 | 0.81539 | 21.9587 | 85.391 | 0 | 3.16 | 6 | HAUL ROAD | 0.094935 | 4486
45645 | 0.81542 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4487
45645 | 0.81544 | 21.9587 | 85.391 | 0 | 3.16 | 6 | HAUL ROAD | 0.094935 | 4488
45645 | 0.81546 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4489
45645 | 0.81549 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4490
45645 | 0.81551 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4491
45645 | 0.81553 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4492
45645 | 0.81556 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4493
45645 | 0.81558 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4494
45645 | 0.8156 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4495
45645 | 0.81563 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4496
45645 | 0.81565 | 21.9587 | 85.3911 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4497
45645 | 0.81567 | 21.9587 | 85.3911 | 0 | 1.39 | 6 | HAUL ROAD | 0.094935 | 4498
45645 | 0.81569 | 21.9588 | 85.3911 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4499
45645 | 0.81572 | 21.9588 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 4500
45645 | 0.81574 | 21.9588 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 0 | 4501
45645 | 0.81576 | 21.9588 | 85.3912 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 4502
45645 | 0.81579 | 21.9588 | 85.3912 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 4503
45645 | 0.81581 | 21.9588 | 85.3913 | 0 | 1.39 | 6 | HAUL ROAD | 10.3126 | 4504
45645 | 0.81583 | 21.9588 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4505
45645 | 0.81586 | 21.9588 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4506
45645 | 0.81588 | 21.9588 | 85.3914 | 0 | 1.39 | 6 | HAUL ROAD | 10.3126 | 4507
45645 | 0.8159 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4508
45645 | 0.81593 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4509
45645 | 0.81595 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4510
45645 | 0.81597 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4511
45645 | 0.816 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4512
45645 | 0.81602 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4513
45645 | 0.81604 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4514
45645 | 0.81606 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4515
45645 | 0.81609 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4516
45645 | 0.81611 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4517
45645 | 0.81613 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4518
45645 | 0.81616 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4519
45645 | 0.81618 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4520
45645 | 0.8162 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4521
45645 | 0.81623 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4522
45645 | 0.81625 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4523
45645 | 0.81627 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4524
45645 | 0.8163 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4525
45645 | 0.81632 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4526
45645 | 0.81634 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4527
45645 | 0.81637 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4528
45645 | 0.81639 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4529
45645 | 0.81641 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4530
45645 | 0.81644 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4531
45645 | 0.81646 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4532
45645 | 0.81648 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4533
45645 | 0.8165 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4534
45645 | 0.81653 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4535
45645 | 0.81655 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4536
45645 | 0.81657 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4537
45645 | 0.8166 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4538
45645 | 0.81662 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4539
45645 | 0.81664 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4540
45645 | 0.81667 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4541
45645 | 0.81669 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4542
45645 | 0.81671 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4543
45645 | 0.81674 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4544
45645 | 0.81676 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4545
45645 | 0.81678 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4546
45645 | 0.81681 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4547
45645 | 0.81683 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4548
45645 | 0.81685 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4549
45645 | 0.81688 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4550
45645 | 0.8169 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4551
45645 | 0.81692 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4552
45645 | 0.81694 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4553
45645 | 0.81697 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4554
45645 | 0.81699 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4555
45645 | 0.81701 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4556
45645 | 0.81704 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4557
45645 | 0.81706 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4558
45645 | 0.81708 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4559
45645 | 0.81711 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4560
45645 | 0.81713 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4561
45645 | 0.81715 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4562
45645 | 0.81718 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4563
45645 | 0.8172 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4564
45645 | 0.81722 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4565
45645 | 0.81725 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4566
45645 | 0.81727 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4567
45645 | 0.81729 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4568
45645 | 0.81731 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4569
45645 | 0.81734 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4570
45645 | 0.81736 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4571
45645 | 0.81738 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4572
45645 | 0.81741 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4573
45645 | 0.81743 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4574
45645 | 0.81745 | 21.9588 | 85.3914 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 4575
45645 | 0.81748 | 21.9588 | 85.3914 | 0 | 21.12 | 6 | HAUL ROAD | 0 | 4576
45645 | 0.8175 | 21.9588 | 85.3914 | 0 | 44.32 | 6 | HAUL ROAD | 0 | 4577
45645 | 0.81752 | 21.9588 | 85.3914 | 0 | 38.88 | 6 | HAUL ROAD | 0 | 4578
45645 | 0.81755 | 21.9588 | 85.3914 | 0 | 30.73 | 6 | HAUL ROAD | 0 | 4579
45645 | 0.81757 | 21.9588 | 85.3914 | 0 | 36.16 | 6 | HAUL ROAD | 0 | 4580
45645 | 0.81759 | 21.9588 | 85.3914 | 0 | 23.79 | 6 | HAUL ROAD | 0 | 4581
45645 | 0.81762 | 21.9588 | 85.3914 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 4582
45645 | 0.81764 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4583
45645 | 0.81766 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4584
45645 | 0.81769 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4585
45645 | 0.81771 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4586
45645 | 0.81773 | 21.9588 | 85.3914 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 4587
45645 | 0.81775 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4588
45645 | 0.81778 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4589
45645 | 0.8178 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4590
45645 | 0.81782 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4591
45645 | 0.81785 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4592
45645 | 0.81787 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4593
45645 | 0.81789 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4594
45645 | 0.81792 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4595
45645 | 0.81794 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4596
45645 | 0.81796 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4597
45645 | 0.81799 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4598
45645 | 0.81801 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4599
45645 | 0.81803 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4600
45645 | 0.81806 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4601
45645 | 0.81808 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4602
45645 | 0.8181 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4603
45645 | 0.81812 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 0 | 4604
45645 | 0.81815 | 21.9588 | 85.3914 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 4605
45645 | 0.81817 | 21.9588 | 85.3914 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 4606
45645 | 0.81819 | 21.9588 | 85.3914 | 0 | 10.12 | 6 | HAUL ROAD | 0 | 4607
45645 | 0.81822 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4608
45645 | 0.81824 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4609
45645 | 0.81826 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4610
45645 | 0.81829 | 21.9588 | 85.3914 | 0 | 15.57 | 6 | HAUL ROAD | 0 | 4611
45645 | 0.81831 | 21.9588 | 85.3914 | 0 | 26.31 | 6 | HAUL ROAD | 0 | 4612
45645 | 0.81833 | 21.9588 | 85.3914 | 0 | 15.57 | 6 | HAUL ROAD | 0 | 4613
45645 | 0.81836 | 21.9588 | 85.3914 | 0 | 15.57 | 6 | HAUL ROAD | 0 | 4614
45645 | 0.81838 | 21.9588 | 85.3914 | 0 | 15.57 | 6 | HAUL ROAD | 0 | 4615
45645 | 0.8184 | 21.9588 | 85.3914 | 0 | 15.57 | 6 | HAUL ROAD | 0 | 4616
45645 | 0.81843 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4617
45645 | 0.81845 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4618
45645 | 0.81847 | 21.9588 | 85.3914 | 0 | 10.12 | 6 | HAUL ROAD | 0 | 4619
45645 | 0.8185 | 21.9588 | 85.3914 | 0 | 10.12 | 6 | HAUL ROAD | 0 | 4620
45645 | 0.81852 | 21.9588 | 85.3914 | 0 | 10.12 | 6 | HAUL ROAD | 0 | 4621
45645 | 0.81854 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4622
45645 | 0.81856 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4623
45645 | 0.81859 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4624
45645 | 0.81861 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4625
45645 | 0.81863 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4626
45645 | 0.81866 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4627
45645 | 0.81868 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4628
45645 | 0.8187 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4629
45645 | 0.81873 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4630
45645 | 0.81875 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4631
45645 | 0.81877 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4632
45645 | 0.8188 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4633
45645 | 0.81882 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4634
45645 | 0.81884 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4635
45645 | 0.81887 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4636
45645 | 0.81889 | 21.9588 | 85.3914 | 0 | 10.12 | 6 | HAUL ROAD | 0 | 4637
45645 | 0.81891 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4638
45645 | 0.81894 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4639
45645 | 0.81896 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4640
45645 | 0.81898 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4641
45645 | 0.819 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4642
45645 | 0.81903 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4643
45645 | 0.81905 | 21.9588 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 0 | 4644
45645 | 0.81907 | 21.9588 | 85.3915 | 0 | 12.8 | 6 | HAUL ROAD | 10.3126 | 4645
45645 | 0.8191 | 21.9588 | 85.3915 | 0 | 15.57 | 6 | HAUL ROAD | 0 | 4646
45645 | 0.81912 | 21.9588 | 85.3915 | 0 | 0 | 6 | HAUL ROAD | 0 | 4647
45645 | 0.81914 | 21.9588 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 4648
45645 | 0.81917 | 21.9588 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4649
45645 | 0.81919 | 21.9589 | 85.3916 | 0 | 10.12 | 6 | HAUL ROAD | 11.1192 | 4650
45645 | 0.81921 | 21.9589 | 85.3915 | 3.16 | 10.12 | 6 | HAUL ROAD | 10.3126 | 4651
45645 | 0.81924 | 21.9589 | 85.3915 | 3.16 | 1.39 | 6 | HAUL ROAD | 0 | 4652
45645 | 0.81926 | 21.9588 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4653
45645 | 0.81928 | 21.9588 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 4654
45645 | 0.81931 | 21.9588 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4655
45645 | 0.81933 | 21.9588 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 0 | 4656
45645 | 0.81935 | 21.9588 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 4657
45645 | 0.81937 | 21.9587 | 85.3911 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4658
45645 | 0.8194 | 21.9587 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4659
45645 | 0.81942 | 21.9586 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 4660
45645 | 0.81944 | 21.9586 | 85.3909 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4661
45645 | 0.81947 | 21.9585 | 85.3908 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4662
45645 | 0.81949 | 21.9584 | 85.3908 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4663
45645 | 0.81951 | 21.9583 | 85.3907 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4664
45645 | 0.81954 | 21.9581 | 85.3907 | 0 | 0 | 6 | HAUL ROAD | 22.239 | 4665
45645 | 0.81956 | 21.958 | 85.3907 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4666
45645 | 0.81958 | 21.9579 | 85.3907 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4667
45645 | 0.81961 | 21.9578 | 85.3908 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4668
45645 | 0.81963 | 21.9577 | 85.3908 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 4669
45645 | 0.81965 | 21.9576 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 23.4323 | 4670
45645 | 0.81968 | 21.9575 | 85.3911 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4671
45645 | 0.8197 | 21.9575 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 4672
45645 | 0.81972 | 21.9575 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 4673
45645 | 0.81975 | 21.9575 | 85.3914 | 0 | 0 | 6 | HAUL ROAD | 10.3126 | 4674
45645 | 0.81977 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 20.6257 | 4675
45645 | 0.81979 | 21.9575 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 0 | 4676
45645 | 0.81981 | 21.9574 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4677
45645 | 0.81984 | 21.9573 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4678
45645 | 0.81986 | 21.9573 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 0.094935 | 4679
45645 | 0.81988 | 21.9572 | 85.3917 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4680
45645 | 0.81991 | 21.9571 | 85.3916 | 0 | 1.39 | 6 | HAUL ROAD | 15.1659 | 4681
45645 | 0.81993 | 21.957 | 85.3916 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 4682
45645 | 0.81995 | 21.9569 | 85.3916 | 0 | 1.39 | 6 | HAUL ROAD | 11.12 | 4683
45645 | 0.81998 | 21.9568 | 85.3915 | 0 | 0 | 6 | HAUL ROAD | 15.1662 | 4684
45645 | 0.82 | 21.9567 | 85.3915 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 4685
45645 | 0.82002 | 21.9566 | 85.3915 | 0 | 1.39 | 6 | HAUL ROAD | 11.1192 | 4686
45645 | 0.82005 | 21.9565 | 85.3914 | 0 | 5.24 | 6 | HAUL ROAD | 15.1656 | 4687
45645 | 0.82007 | 21.9564 | 85.3914 | 0 | 12.8 | 6 | HAUL ROAD | 11.1196 | 4688
45645 | 0.82009 | 21.9563 | 85.3913 | 0 | 3.16 | 6 | HAUL ROAD | 15.1659 | 4689
45645 | 0.82012 | 21.9562 | 85.3913 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4690
45645 | 0.82014 | 21.9561 | 85.3912 | 0 | 0 | 6 | HAUL ROAD | 15.1656 | 4691
45645 | 0.82016 | 21.956 | 85.3911 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4692
45645 | 0.82019 | 21.9559 | 85.3911 | 0 | 1.39 | 6 | HAUL ROAD | 11.1192 | 4693
45645 | 0.82021 | 21.9558 | 85.391 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4694
45645 | 0.82023 | 21.9557 | 85.391 | 0 | 3.16 | 6 | HAUL ROAD | 11.1196 | 4695
45645 | 0.82025 | 21.9556 | 85.3909 | 0 | 1.39 | 6 | HAUL ROAD | 15.1659 | 4696
45645 | 0.82028 | 21.9555 | 85.3909 | 0 | 3.16 | 6 | HAUL ROAD | 11.1192 | 4697
45645 | 0.8203 | 21.9554 | 85.3908 | 0 | 5.24 | 6 | HAUL ROAD | 15.1659 | 4698
45645 | 0.82032 | 21.9552 | 85.3908 | 0 | 0 | 6 | HAUL ROAD | 22.239 | 4699
45645 | 0.82035 | 21.9551 | 85.3908 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 4700
45645 | 0.82037 | 21.955 | 85.3907 | 0 | 26.31 | 6 | HAUL ROAD | 15.1659 | 4701
45645 | 0.82039 | 21.9549 | 85.3906 | 0 | 36.16 | 6 | HAUL ROAD | 15.1659 | 4702
45645 | 0.82042 | 21.9548 | 85.3906 | 0 | 23.79 | 6 | HAUL ROAD | 11.1196 | 4703
45645 | 0.82044 | 21.9547 | 85.3905 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4704
45645 | 0.82046 | 21.9546 | 85.3905 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4705
45645 | 0.82049 | 21.9545 | 85.3904 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4706
45645 | 0.82051 | 21.9544 | 85.3904 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 4707
45645 | 0.82053 | 21.9543 | 85.3903 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4708
45645 | 0.82056 | 21.9542 | 85.3903 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 4709
45645 | 0.82058 | 21.9541 | 85.3903 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4710
45645 | 0.8206 | 21.954 | 85.3902 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4711
45645 | 0.82063 | 21.9539 | 85.3902 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4712
45645 | 0.82065 | 21.9538 | 85.3901 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4713
45645 | 0.82067 | 21.9537 | 85.3901 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4714
45645 | 0.82069 | 21.9536 | 85.3901 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 4715
45645 | 0.82072 | 21.9535 | 85.39 | 0 | 0 | 6 | HAUL ROAD | 15.1659 | 4716
45645 | 0.82074 | 21.9535 | 85.39 | 0 | 0 | 6 | HAUL ROAD | 0 | 4717
45645 | 0.82076 | 21.9534 | 85.39 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 4718
45645 | 0.82079 | 21.9533 | 85.3899 | 0 | 0 | 6 | HAUL ROAD | 15.1662 | 4719
45645 | 0.82081 | 21.9532 | 85.3899 | 0 | 3.16 | 6 | HAUL ROAD | 11.1196 | 4720
45645 | 0.82083 | 21.9531 | 85.3899 | 23.79 | 57.92 | 6 | HAUL ROAD | 11.1196 | 4721
45645 | 0.82086 | 21.953 | 85.3898 | 90.59 | 0 | 6 | HAUL ROAD | 15.1662 | 4722
45645 | 0.82088 | 21.9529 | 85.3898 | 7.58 | 18.36 | 6 | HAUL ROAD | 11.1192 | 4723
45645 | 0.8209 | 21.9528 | 85.3897 | 1.39 | 1.39 | 6 | HAUL ROAD | 15.1659 | 4724
45645 | 0.82093 | 21.9528 | 85.3897 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 4725
45645 | 0.82095 | 21.9527 | 85.3896 | 10.12 | 7.58 | 6 | HAUL ROAD | 15.1659 | 4726
45645 | 0.82097 | 21.9526 | 85.3896 | 41.6 | 10.12 | 6 | HAUL ROAD | 11.1192 | 4727
45645 | 0.821 | 21.9525 | 85.3896 | 15.57 | 30.73 | 6 | HAUL ROAD | 11.1192 | 4728
45645 | 0.82102 | 21.9524 | 85.3896 | 12.8 | 30.73 | 6 | HAUL ROAD | 11.1196 | 4729
45645 | 0.82104 | 21.9522 | 85.3896 | 38.88 | 49.76 | 6 | HAUL ROAD | 22.2388 | 4730
45645 | 0.82106 | 21.9521 | 85.3896 | 23.79 | 76.97 | 6 | HAUL ROAD | 11.1192 | 4731
45645 | 0.82109 | 21.952 | 85.3896 | 279.61 | 10.12 | 6 | HAUL ROAD | 11.1196 | 4732
45645 | 0.82111 | 21.9519 | 85.3896 | 5.24 | 3.16 | 6 | HAUL ROAD | 11.1192 | 4733
45645 | 0.82113 | 21.9518 | 85.3895 | 5.24 | 7.58 | 6 | HAUL ROAD | 15.1659 | 4734
45645 | 0.82116 | 21.9517 | 85.3895 | 10.12 | 10.12 | 6 | HAUL ROAD | 11.1196 | 4735
45645 | 0.82118 | 21.9516 | 85.3895 | 10.12 | 7.58 | 6 | HAUL ROAD | 11.12 | 4736
45645 | 0.8212 | 21.9515 | 85.3895 | 7.58 | 10.12 | 6 | HAUL ROAD | 11.1192 | 4737
45645 | 0.82123 | 21.9514 | 85.3895 | 12.8 | 7.58 | 6 | HAUL ROAD | 11.1196 | 4738
45645 | 0.82125 | 21.9513 | 85.3894 | 3.16 | 7.58 | 6 | HAUL ROAD | 15.1662 | 4739
45645 | 0.82127 | 21.9512 | 85.3894 | 5.24 | 7.58 | 6 | HAUL ROAD | 11.1192 | 4740
45645 | 0.8213 | 21.9511 | 85.3894 | 3.16 | 10.12 | 6 | HAUL ROAD | 11.1196 | 4741
45645 | 0.82132 | 21.951 | 85.3893 | 1.39 | 12.8 | 6 | HAUL ROAD | 15.1659 | 4742
45645 | 0.82134 | 21.9509 | 85.3893 | 0 | 10.12 | 6 | HAUL ROAD | 11.1196 | 4743
45645 | 0.82137 | 21.9508 | 85.3892 | 0 | 7.58 | 6 | HAUL ROAD | 15.1659 | 4744
45645 | 0.82139 | 21.9508 | 85.3892 | 1.39 | 7.58 | 6 | HAUL ROAD | 0 | 4745
45645 | 0.82141 | 21.9507 | 85.3891 | 0 | 5.24 | 6 | HAUL ROAD | 15.1662 | 4746
45645 | 0.82144 | 21.9506 | 85.389 | 0 | 3.16 | 6 | HAUL ROAD | 15.1659 | 4747
45645 | 0.82146 | 21.9505 | 85.389 | 1.39 | 7.58 | 6 | HAUL ROAD | 11.1192 | 4748
45645 | 0.82148 | 21.9504 | 85.3889 | 0 | 1.39 | 6 | HAUL ROAD | 15.1659 | 4749
45645 | 0.8215 | 21.9503 | 85.3888 | 5.24 | 0 | 6 | HAUL ROAD | 15.1662 | 4750
45645 | 0.82153 | 21.9503 | 85.3887 | 1.39 | 1.39 | 6 | HAUL ROAD | 10.3135 | 4751
45645 | 0.82155 | 21.9502 | 85.3887 | 1.39 | 0 | 6 | HAUL ROAD | 11.1196 | 4752
45645 | 0.82157 | 21.9502 | 85.3886 | 0 | 0 | 6 | HAUL ROAD | 10.3139 | 4753
45645 | 0.8216 | 21.9501 | 85.3885 | 0 | 0 | 6 | HAUL ROAD | 15.1662 | 4754
45645 | 0.82162 | 21.9501 | 85.3884 | 0 | 0 | 6 | HAUL ROAD | 10.3139 | 4755
45645 | 0.82164 | 21.9501 | 85.3882 | 0 | 0 | 6 | HAUL ROAD | 20.6272 | 4756
45645 | 0.82167 | 21.9501 | 85.3881 | 0 | 0 | 6 | HAUL ROAD | 10.3139 | 4757
45645 | 0.82169 | 21.95 | 85.388 | 0 | 0 | 6 | HAUL ROAD | 15.1662 | 4758
45645 | 0.82171 | 21.95 | 85.3879 | 26.31 | 7.58 | 6 | HAUL ROAD | 10.3139 | 4759
45645 | 0.82174 | 21.9499 | 85.3879 | 49.76 | 1.39 | 6 | HAUL ROAD | 11.1196 | 4760
45645 | 0.82176 | 21.9498 | 85.3878 | 7.58 | 10.12 | 6 | HAUL ROAD | 15.1665 | 4761
45645 | 0.82178 | 21.9497 | 85.3877 | 55.2 | 1.39 | 6 | HAUL ROAD | 15.1662 | 4762
45645 | 0.82181 | 21.9497 | 85.3877 | 68.8 | 30.73 | 6 | HAUL ROAD | 0 | 4763
45645 | 0.82183 | 21.9495 | 85.3876 | 33.45 | 10.12 | 6 | HAUL ROAD | 24.5139 | 4764
45645 | 0.82185 | 21.9494 | 85.3876 | 93.32 | 10.12 | 6 | HAUL ROAD | 11.1192 | 4765
45645 | 0.82188 | 21.9493 | 85.3875 | 36.16 | 12.8 | 6 | HAUL ROAD | 15.1659 | 4766
45645 | 0.8219 | 21.9492 | 85.3875 | 21.12 | 7.58 | 6 | HAUL ROAD | 11.1192 | 4767
45645 | 0.82192 | 21.9491 | 85.3875 | 36.16 | 7.58 | 6 | HAUL ROAD | 11.1196 | 4768
45645 | 0.82194 | 21.949 | 85.3875 | 33.45 | 23.79 | 6 | HAUL ROAD | 11.1196 | 4769
45645 | 0.82197 | 21.9489 | 85.3874 | 33.45 | 18.36 | 6 | HAUL ROAD | 15.1662 | 4770
45645 | 0.82199 | 21.9488 | 85.3874 | 0 | 3.16 | 6 | HAUL ROAD | 11.1192 | 4771
45645 | 0.82201 | 21.9487 | 85.3874 | 26.31 | 23.79 | 6 | HAUL ROAD | 11.1196 | 4772
45645 | 0.82204 | 21.9486 | 85.3874 | 30.73 | 0 | 6 | HAUL ROAD | 11.12 | 4773
45645 | 0.82206 | 21.9485 | 85.3874 | 0 | 7.58 | 6 | HAUL ROAD | 11.1196 | 4774
45645 | 0.82208 | 21.9483 | 85.3873 | 5.24 | 21.12 | 6 | HAUL ROAD | 24.5141 | 4775
45645 | 0.82211 | 21.9482 | 85.3873 | 26.31 | 1.39 | 6 | HAUL ROAD | 11.1192 | 4776
45645 | 0.82213 | 21.9481 | 85.3873 | 10.12 | 3.16 | 6 | HAUL ROAD | 11.1192 | 4777
45645 | 0.82215 | 21.948 | 85.3873 | 5.24 | 7.58 | 6 | HAUL ROAD | 11.1196 | 4778
45645 | 0.82218 | 21.9479 | 85.3872 | 12.8 | 7.58 | 6 | HAUL ROAD | 15.1659 | 4779
45645 | 0.8222 | 21.9478 | 85.3872 | 3.16 | 10.12 | 6 | HAUL ROAD | 11.1196 | 4780
45645 | 0.82222 | 21.9477 | 85.3872 | 15.57 | 12.8 | 6 | HAUL ROAD | 11.12 | 4781
45645 | 0.82225 | 21.9477 | 85.3872 | 10.12 | 36.16 | 6 | HAUL ROAD | 0 | 4782
45645 | 0.82227 | 21.9476 | 85.3871 | 18.36 | 10.12 | 6 | HAUL ROAD | 15.1665 | 4783
45645 | 0.82229 | 21.9475 | 85.3871 | 7.58 | 18.36 | 6 | HAUL ROAD | 11.1196 | 4784
45645 | 0.82231 | 21.9474 | 85.3871 | 26.31 | 5.24 | 6 | HAUL ROAD | 11.1192 | 4785
45645 | 0.82234 | 21.9473 | 85.3871 | 1.39 | 10.12 | 6 | HAUL ROAD | 11.12 | 4786
45645 | 0.82236 | 21.9472 | 85.387 | 18.36 | 10.12 | 6 | HAUL ROAD | 15.1665 | 4787
45645 | 0.82238 | 21.9472 | 85.387 | 5.24 | 10.12 | 6 | HAUL ROAD | 0 | 4788
45645 | 0.82241 | 21.9471 | 85.387 | 18.36 | 1.39 | 6 | HAUL ROAD | 11.1192 | 4789
45645 | 0.82243 | 21.9471 | 85.3869 | 5.24 | 3.16 | 6 | HAUL ROAD | 10.3139 | 4790
45645 | 0.82245 | 21.947 | 85.3869 | 1.39 | 12.8 | 6 | HAUL ROAD | 11.1196 | 4791
45645 | 0.82248 | 21.9469 | 85.3869 | 21.12 | 10.12 | 6 | HAUL ROAD | 11.1192 | 4792
45645 | 0.8225 | 21.9469 | 85.3869 | 5.24 | 3.16 | 6 | HAUL ROAD | 0 | 4793
45645 | 0.82252 | 21.9469 | 85.3868 | 7.58 | 18.36 | 6 | HAUL ROAD | 10.3139 | 4794
45645 | 0.82255 | 21.9469 | 85.3867 | 49.76 | 10.12 | 6 | HAUL ROAD | 10.3139 | 4795
45645 | 0.82257 | 21.9469 | 85.3866 | 57.92 | 38.88 | 6 | HAUL ROAD | 10.3139 | 4796
45645 | 0.82259 | 21.9469 | 85.3865 | 82.42 | 5.24 | 6 | HAUL ROAD | 10.3139 | 4797
45645 | 0.82262 | 21.947 | 85.3864 | 49.76 | 18.36 | 6 | HAUL ROAD | 15.1665 | 4798
45645 | 0.82264 | 21.947 | 85.3863 | 44.32 | 18.36 | 6 | HAUL ROAD | 10.3144 | 4799
45645 | 0.82266 | 21.947 | 85.3862 | 38.88 | 23.79 | 6 | HAUL ROAD | 10.3144 | 4800
45645 | 0.82269 | 21.9471 | 85.3861 | 60.64 | 18.36 | 6 | HAUL ROAD | 15.1665 | 4801
45645 | 0.82271 | 21.9471 | 85.386 | 55.2 | 21.12 | 6 | HAUL ROAD | 10.3139 | 4802
45645 | 0.82273 | 21.9472 | 85.3859 | 55.2 | 26.31 | 6 | HAUL ROAD | 15.1665 | 4803
45645 | 0.82275 | 21.9472 | 85.3858 | 85.14 | 3.16 | 6 | HAUL ROAD | 10.3139 | 4804
45645 | 0.82278 | 21.9472 | 85.3857 | 60.64 | 33.45 | 6 | HAUL ROAD | 10.3139 | 4805
45645 | 0.8228 | 21.9473 | 85.3856 | 82.42 | 5.24 | 6 | HAUL ROAD | 15.1665 | 4806
45645 | 0.82282 | 21.9473 | 85.3855 | 57.92 | 26.31 | 6 | HAUL ROAD | 10.3144 | 4807
45645 | 0.82285 | 21.9472 | 85.3854 | 98.77 | 30.73 | 6 | HAUL ROAD | 15.1665 | 4808
45645 | 0.82287 | 21.9471 | 85.3853 | 5.24 | 3.16 | 6 | HAUL ROAD | 15.1665 | 4809
45645 | 0.82289 | 21.947 | 85.3853 | 60.64 | 33.45 | 6 | HAUL ROAD | 11.1196 | 4810
45645 | 0.82292 | 21.9469 | 85.3852 | 93.32 | 15.57 | 6 | HAUL ROAD | 15.1665 | 4811
45645 | 0.82294 | 21.9468 | 85.3852 | 96.05 | 18.36 | 6 | HAUL ROAD | 11.1196 | 4812
45645 | 0.82296 | 21.9467 | 85.3851 | 66.08 | 41.6 | 6 | HAUL ROAD | 15.1665 | 4813
45645 | 0.82299 | 21.9466 | 85.3851 | 131.52 | 26.31 | 6 | HAUL ROAD | 11.1196 | 4814
45645 | 0.82301 | 21.9465 | 85.385 | 66.08 | 38.88 | 6 | HAUL ROAD | 15.1665 | 4815
45645 | 0.82303 | 21.9464 | 85.385 | 85.14 | 7.58 | 6 | HAUL ROAD | 11.1196 | 4816
45645 | 0.82306 | 21.9463 | 85.385 | 76.97 | 23.79 | 6 | HAUL ROAD | 11.1196 | 4817
45645 | 0.82308 | 21.9462 | 85.3849 | 66.08 | 5.24 | 6 | HAUL ROAD | 15.1665 | 4818
45645 | 0.8231 | 21.9461 | 85.3849 | 26.31 | 12.8 | 6 | HAUL ROAD | 11.1196 | 4819
45645 | 0.82312 | 21.946 | 85.3849 | 21.12 | 18.36 | 6 | HAUL ROAD | 11.1196 | 4820
45645 | 0.82315 | 21.9459 | 85.3849 | 38.88 | 15.57 | 6 | HAUL ROAD | 11.1196 | 4821
45645 | 0.82317 | 21.9458 | 85.3848 | 26.31 | 23.79 | 6 | HAUL ROAD | 15.1665 | 4822
45645 | 0.82319 | 21.9457 | 85.3848 | 5.24 | 12.8 | 6 | HAUL ROAD | 11.1192 | 4823
45645 | 0.82322 | 21.9456 | 85.3848 | 30.73 | 12.8 | 6 | HAUL ROAD | 11.1196 | 4824
45645 | 0.82324 | 21.9454 | 85.3848 | 26.31 | 18.36 | 6 | HAUL ROAD | 22.239 | 4825
45645 | 0.82326 | 21.9453 | 85.3848 | 44.32 | 15.57 | 6 | HAUL ROAD | 11.1196 | 4826
45645 | 0.82329 | 21.9452 | 85.3848 | 44.32 | 30.73 | 6 | HAUL ROAD | 11.1192 | 4827
45645 | 0.82331 | 21.9451 | 85.3848 | 60.64 | 26.31 | 6 | HAUL ROAD | 11.1192 | 4828
45645 | 0.82333 | 21.945 | 85.3848 | 66.08 | 18.36 | 6 | HAUL ROAD | 11.1196 | 4829
45645 | 0.82336 | 21.9449 | 85.3848 | 30.73 | 10.12 | 6 | HAUL ROAD | 11.1196 | 4830
45645 | 0.82338 | 21.9447 | 85.3848 | 18.36 | 12.8 | 6 | HAUL ROAD | 22.239 | 4831
45645 | 0.8234 | 21.9446 | 85.3848 | 5.24 | 7.58 | 6 | HAUL ROAD | 11.1192 | 4832
45645 | 0.82343 | 21.9445 | 85.3847 | 3.16 | 7.58 | 6 | HAUL ROAD | 15.1665 | 4833
45645 | 0.82345 | 21.9444 | 85.3847 | 12.8 | 12.8 | 6 | HAUL ROAD | 11.1192 | 4834
45645 | 0.82347 | 21.9443 | 85.3847 | 23.79 | 15.57 | 6 | HAUL ROAD | 11.1196 | 4835
45645 | 0.8235 | 21.9443 | 85.3847 | 26.31 | 26.31 | 6 | HAUL ROAD | 0.094935 | 4836
45645 | 0.82352 | 21.9442 | 85.3847 | 44.32 | 26.31 | 6 | HAUL ROAD | 11.12 | 4837
45645 | 0.82354 | 21.9442 | 85.3846 | 44.32 | 23.79 | 6 | HAUL ROAD | 10.3144 | 4838
45645 | 0.82356 | 21.9441 | 85.3846 | 71.53 | 47.04 | 6 | HAUL ROAD | 11.1192 | 4839
45645 | 0.82359 | 21.9441 | 85.3846 | 82.42 | 30.73 | 6 | HAUL ROAD | 0 | 4840
45645 | 0.82361 | 21.944 | 85.3846 | 74.25 | 12.8 | 6 | HAUL ROAD | 11.1196 | 4841
45645 | 0.82363 | 21.9439 | 85.3847 | 38.88 | 1.39 | 6 | HAUL ROAD | 15.1665 | 4842
45645 | 0.82366 | 21.9439 | 85.3848 | 15.57 | 0 | 6 | HAUL ROAD | 10.3135 | 4843
45645 | 0.82368 | 21.9438 | 85.3848 | 5.24 | 1.39 | 6 | HAUL ROAD | 11.1196 | 4844
45645 | 0.8237 | 21.9438 | 85.3849 | 0 | 0 | 6 | HAUL ROAD | 10.3144 | 4845
45645 | 0.82373 | 21.9437 | 85.3849 | 0 | 3.16 | 6 | HAUL ROAD | 11.1196 | 4846
45645 | 0.82375 | 21.9436 | 85.385 | 0 | 5.24 | 6 | HAUL ROAD | 15.1662 | 4847
45645 | 0.82377 | 21.9436 | 85.385 | 0 | 10.12 | 6 | HAUL ROAD | 0 | 4848
45645 | 0.8238 | 21.9435 | 85.385 | 0 | 21.12 | 6 | HAUL ROAD | 11.1192 | 4849
45645 | 0.82382 | 21.9434 | 85.3851 | 10.12 | 3.16 | 6 | HAUL ROAD | 15.1662 | 4850
45645 | 0.82384 | 21.9434 | 85.3851 | 1.39 | 1.39 | 6 | HAUL ROAD | 0 | 4851
45645 | 0.82387 | 21.9433 | 85.3851 | 5.24 | 21.12 | 6 | HAUL ROAD | 11.1192 | 4852
45645 | 0.82389 | 21.9433 | 85.3852 | 18.36 | 18.36 | 6 | HAUL ROAD | 10.3139 | 4853
45645 | 0.82391 | 21.9432 | 85.3852 | 5.24 | 18.36 | 6 | HAUL ROAD | 11.1192 | 4854
45645 | 0.82394 | 21.9431 | 85.3852 | 12.8 | 3.16 | 6 | HAUL ROAD | 11.1192 | 4855
45645 | 0.82396 | 21.943 | 85.3852 | 0 | 3.16 | 6 | HAUL ROAD | 11.12 | 4856
45645 | 0.82398 | 21.943 | 85.3852 | 0 | 3.16 | 6 | HAUL ROAD | 0.094935 | 4857
45645 | 0.824 | 21.9429 | 85.3852 | 1.39 | 5.24 | 6 | HAUL ROAD | 11.1196 | 4858
45645 | 0.82403 | 21.9428 | 85.3852 | 1.39 | 12.8 | 6 | HAUL ROAD | 11.12 | 4859
45645 | 0.82405 | 21.9427 | 85.3852 | 7.58 | 15.57 | 6 | HAUL ROAD | 11.12 | 4860
45645 | 0.82407 | 21.9427 | 85.3852 | 10.12 | 12.8 | 6 | HAUL ROAD | 0 | 4861
45645 | 0.8241 | 21.9426 | 85.3852 | 7.58 | 3.16 | 6 | HAUL ROAD | 11.12 | 4862
45645 | 0.82412 | 21.9425 | 85.3852 | 3.16 | 7.58 | 6 | HAUL ROAD | 11.1192 | 4863
45645 | 0.82414 | 21.9425 | 85.3851 | 12.8 | 7.58 | 6 | HAUL ROAD | 10.3135 | 4864
45645 | 0.82417 | 21.9424 | 85.385 | 10.12 | 10.12 | 6 | HAUL ROAD | 15.1665 | 4865
45645 | 0.82419 | 21.9424 | 85.3849 | 10.12 | 18.36 | 6 | HAUL ROAD | 10.3139 | 4866
45645 | 0.82421 | 21.9423 | 85.3849 | 18.36 | 18.36 | 6 | HAUL ROAD | 11.1192 | 4867
45645 | 0.82424 | 21.9423 | 85.3849 | 21.12 | 15.57 | 6 | HAUL ROAD | 0 | 4868
45645 | 0.82426 | 21.9422 | 85.3849 | 10.12 | 10.12 | 6 | HAUL ROAD | 11.1192 | 4869
45645 | 0.82428 | 21.9421 | 85.385 | 3.16 | 5.24 | 6 | HAUL ROAD | 15.1665 | 4870
45645 | 0.82431 | 21.9421 | 85.385 | 5.24 | 5.24 | 6 | HAUL ROAD | 0.094935 | 4871
45645 | 0.82433 | 21.9421 | 85.3851 | 3.16 | 3.16 | 6 | HAUL ROAD | 10.3144 | 4872
45645 | 0.82435 | 21.9421 | 85.3852 | 7.58 | 5.24 | 6 | HAUL ROAD | 10.3144 | 4873
45645 | 0.82437 | 21.9421 | 85.3853 | 3.16 | 7.58 | 6 | HAUL ROAD | 10.3144 | 4874
45645 | 0.8244 | 21.9421 | 85.3854 | 7.58 | 5.24 | 6 | HAUL ROAD | 10.3144 | 4875
45645 | 0.82442 | 21.9421 | 85.3855 | 10.12 | 10.12 | 6 | HAUL ROAD | 10.3144 | 4876
45645 | 0.82444 | 21.9421 | 85.3856 | 30.73 | 18.36 | 6 | HAUL ROAD | 10.3144 | 4877
45645 | 0.82447 | 21.9422 | 85.3857 | 26.31 | 3.16 | 6 | HAUL ROAD | 15.1665 | 4878
45645 | 0.82449 | 21.9422 | 85.3858 | 10.12 | 3.16 | 6 | HAUL ROAD | 10.3139 | 4879
45645 | 0.82451 | 21.9423 | 85.3858 | 1.39 | 1.39 | 6 | HAUL ROAD | 11.1192 | 4880
45645 | 0.82454 | 21.9423 | 85.3859 | 7.58 | 5.24 | 6 | HAUL ROAD | 10.3135 | 4881
45645 | 0.82456 | 21.9423 | 85.386 | 12.8 | 3.16 | 6 | HAUL ROAD | 10.3135 | 4882
45645 | 0.82458 | 21.9423 | 85.386 | 12.8 | 7.58 | 6 | HAUL ROAD | 0 | 4883
45645 | 0.82461 | 21.9423 | 85.3861 | 15.57 | 7.58 | 6 | HAUL ROAD | 10.3135 | 4884
45645 | 0.82463 | 21.9424 | 85.3862 | 18.36 | 3.16 | 6 | HAUL ROAD | 15.1662 | 4885
45645 | 0.82465 | 21.9424 | 85.3863 | 10.12 | 10.12 | 6 | HAUL ROAD | 10.3139 | 4886
45645 | 0.82468 | 21.9424 | 85.3864 | 7.58 | 18.36 | 6 | HAUL ROAD | 10.3139 | 4887
45645 | 0.8247 | 21.9425 | 85.3865 | 23.79 | 33.45 | 6 | HAUL ROAD | 15.1665 | 4888
45645 | 0.82472 | 21.9425 | 85.3865 | 47.04 | 30.73 | 6 | HAUL ROAD | 0 | 4889
45645 | 0.82475 | 21.9425 | 85.3866 | 26.31 | 7.58 | 6 | HAUL ROAD | 10.3135 | 4890
45645 | 0.82477 | 21.9425 | 85.3867 | 0 | 0 | 6 | HAUL ROAD | 10.3135 | 4891
45645 | 0.82479 | 21.9425 | 85.3868 | 47.04 | 1.39 | 6 | HAUL ROAD | 10.3135 | 4892
45645 | 0.82481 | 21.9424 | 85.3869 | 15.57 | 0 | 6 | HAUL ROAD | 15.1665 | 4893
45645 | 0.82484 | 21.9424 | 85.3869 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 4894
45645 | 0.82486 | 21.9424 | 85.387 | 0 | 1.39 | 6 | HAUL ROAD | 10.3139 | 4895
45645 | 0.82488 | 21.9424 | 85.387 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 4896
45645 | 0.82491 | 21.9424 | 85.3871 | 0 | 3.16 | 6 | HAUL ROAD | 10.3139 | 4897
45645 | 0.82493 | 21.9423 | 85.3872 | 3.16 | 12.8 | 6 | HAUL ROAD | 15.1662 | 4898
45645 | 0.82495 | 21.9423 | 85.3872 | 21.12 | 30.73 | 6 | HAUL ROAD | 0 | 4899
45645 | 0.82498 | 21.9423 | 85.3873 | 60.64 | 10.12 | 6 | HAUL ROAD | 10.3135 | 4900
45645 | 0.825 | 21.9422 | 85.3873 | 41.6 | 18.36 | 17 | REST SHELTER | 11.1192 | 4901
45645 | 0.82502 | 21.9421 | 85.3874 | 18.36 | 44.32 | 6 | HAUL ROAD | 15.1665 | 4902
45645 | 0.82505 | 21.9421 | 85.3874 | 57.92 | 101.5 | 6 | HAUL ROAD | 0.094935 | 4903
45645 | 0.82507 | 21.942 | 85.3874 | 136.99 | 79.7 | 17 | REST SHELTER | 11.12 | 4904
45645 | 0.82509 | 21.9419 | 85.3873 | 106.96 | 60.64 | 17 | REST SHELTER | 15.1665 | 4905
45645 | 0.82512 | 21.9419 | 85.3873 | 36.16 | 41.6 | 17 | REST SHELTER | 0.094935 | 4906
45645 | 0.82514 | 21.9418 | 85.3873 | 18.36 | 26.31 | 6 | HAUL ROAD | 11.1196 | 4907
45645 | 0.82516 | 21.9418 | 85.3872 | 12.8 | 33.45 | 6 | HAUL ROAD | 10.3139 | 4908
45645 | 0.82519 | 21.9417 | 85.3872 | 26.31 | 33.45 | 6 | HAUL ROAD | 11.1196 | 4909
45645 | 0.82521 | 21.9416 | 85.3872 | 10.12 | 15.57 | 6 | HAUL ROAD | 11.1196 | 4910
45645 | 0.82523 | 21.9415 | 85.3871 | 36.16 | 30.73 | 6 | HAUL ROAD | 15.1665 | 4911
45645 | 0.82525 | 21.9415 | 85.3871 | 47.04 | 23.79 | 6 | HAUL ROAD | 0 | 4912
45645 | 0.82528 | 21.9414 | 85.3871 | 44.32 | 47.04 | 6 | HAUL ROAD | 11.1192 | 4913
45645 | 0.8253 | 21.9413 | 85.3871 | 115.14 | 109.68 | 6 | HAUL ROAD | 11.1196 | 4914
45645 | 0.82532 | 21.9412 | 85.3872 | 7.58 | 7.58 | 6 | HAUL ROAD | 15.1665 | 4915
45645 | 0.82535 | 21.9411 | 85.3872 | 10.12 | 1.39 | 19 | DUMPER TERMINAL PARKING | 11.1196 | 4916
45645 | 0.82537 | 21.941 | 85.3872 | 7.58 | 18.36 | 6 | HAUL ROAD | 11.1192 | 4917
45645 | 0.82539 | 21.941 | 85.3871 | 139.72 | 41.6 | 6 | HAUL ROAD | 10.3139 | 4918
45645 | 0.82542 | 21.9409 | 85.387 | 96.05 | 85.14 | 6 | HAUL ROAD | 15.1668 | 4919
45645 | 0.82544 | 21.9408 | 85.3869 | 224.62 | 7.58 | 9 | DUMPER TERMINAL PATHWAY | 15.1665 | 4920
45645 | 0.82546 | 21.9407 | 85.3868 | 126.06 | 76.97 | 9 | DUMPER TERMINAL PATHWAY | 15.1665 | 4921
45645 | 0.82549 | 21.9406 | 85.3867 | 74.25 | 21.12 | 9 | DUMPER TERMINAL PATHWAY | 15.1665 | 4922
45645 | 0.82551 | 21.9406 | 85.3866 | 210.9 | 7.58 | 6 | HAUL ROAD | 10.3144 | 4923
45645 | 0.82553 | 21.9405 | 85.3865 | 126.06 | 66.08 | 19 | DUMPER TERMINAL PARKING | 15.1668 | 4924
45645 | 0.82556 | 21.9404 | 85.3864 | 52.48 | 15.57 | 19 | DUMPER TERMINAL PARKING | 15.1668 | 4925
45645 | 0.82558 | 21.9403 | 85.3863 | 199.93 | 3.16 | 19 | DUMPER TERMINAL PARKING | 15.1668 | 4926
45645 | 0.8256 | 21.9403 | 85.3862 | 139.72 | 76.97 | 19 | DUMPER TERMINAL PARKING | 10.3144 | 4927
45645 | 0.82563 | 21.9402 | 85.3861 | 85.14 | 79.7 | 6 | HAUL ROAD | 15.1668 | 4928
45645 | 0.82565 | 21.9402 | 85.386 | 205.42 | 18.36 | 6 | HAUL ROAD | 10.3139 | 4929
45645 | 0.82567 | 21.9401 | 85.3859 | 172.54 | 41.6 | 6 | HAUL ROAD | 15.1668 | 4930
45645 | 0.82569 | 21.94 | 85.3858 | 180.75 | 63.36 | 6 | HAUL ROAD | 15.1665 | 4931
45645 | 0.82572 | 21.94 | 85.3857 | 147.92 | 93.32 | 6 | HAUL ROAD | 10.3144 | 4932
45645 | 0.82574 | 21.9399 | 85.3855 | 134.25 | 21.12 | 6 | HAUL ROAD | 23.4342 | 4933
45645 | 0.82576 | 21.9399 | 85.3854 | 126.06 | 12.8 | 6 | HAUL ROAD | 10.3144 | 4934
45645 | 0.82579 | 21.9398 | 85.3853 | 87.87 | 63.36 | 6 | HAUL ROAD | 15.1665 | 4935
45645 | 0.82581 | 21.9397 | 85.3853 | 126.06 | 5.24 | 6 | HAUL ROAD | 11.1196 | 4936
45645 | 0.82583 | 21.9396 | 85.3852 | 221.88 | 5.24 | 6 | HAUL ROAD | 15.1668 | 4937
45645 | 0.82586 | 21.9395 | 85.3851 | 139.72 | 109.68 | 6 | HAUL ROAD | 15.1668 | 4938
45645 | 0.82588 | 21.9394 | 85.385 | 76.97 | 3.16 | 6 | HAUL ROAD | 15.1671 | 4939
45645 | 0.8259 | 21.9394 | 85.3849 | 205.42 | 55.2 | 6 | HAUL ROAD | 10.3144 | 4940
45645 | 0.82593 | 21.9393 | 85.3848 | 188.97 | 60.64 | 6 | HAUL ROAD | 15.1665 | 4941
45645 | 0.82595 | 21.9393 | 85.3846 | 156.12 | 120.6 | 6 | HAUL ROAD | 20.6285 | 4942
45645 | 0.82597 | 21.9393 | 85.3845 | 134.25 | 7.58 | 6 | HAUL ROAD | 10.3144 | 4943
45645 | 0.826 | 21.9393 | 85.3844 | 117.87 | 106.96 | 6 | HAUL ROAD | 10.3144 | 4944
45645 | 0.82602 | 21.9394 | 85.3843 | 93.32 | 7.58 | 6 | HAUL ROAD | 15.1665 | 4945
45645 | 0.82604 | 21.9394 | 85.3841 | 85.14 | 98.77 | 6 | HAUL ROAD | 20.6287 | 4946
45645 | 0.82606 | 21.9394 | 85.384 | 156.12 | 12.8 | 6 | HAUL ROAD | 10.3144 | 4947
45645 | 0.82609 | 21.9394 | 85.3839 | 169.8 | 85.14 | 6 | HAUL ROAD | 10.3144 | 4948
45645 | 0.82611 | 21.9394 | 85.3838 | 68.8 | 3.16 | 6 | HAUL ROAD | 10.3144 | 4949
45645 | 0.82613 | 21.9394 | 85.3836 | 26.31 | 10.12 | 6 | HAUL ROAD | 20.6287 | 4950
45645 | 0.82616 | 21.9394 | 85.3835 | 60.64 | 12.8 | 6 | HAUL ROAD | 10.3144 | 4951
45645 | 0.82618 | 21.9394 | 85.3834 | 60.64 | 18.36 | 6 | HAUL ROAD | 10.3144 | 4952
45645 | 0.8262 | 21.9393 | 85.3833 | 68.8 | 12.8 | 6 | HAUL ROAD | 15.1665 | 4953
45645 | 0.82623 | 21.9392 | 85.3832 | 44.32 | 10.12 | 6 | HAUL ROAD | 15.1668 | 4954
45645 | 0.82625 | 21.9391 | 85.3831 | 23.79 | 7.58 | 6 | HAUL ROAD | 15.1668 | 4955
45645 | 0.82627 | 21.9391 | 85.383 | 26.31 | 10.12 | 6 | HAUL ROAD | 10.3144 | 4956
45645 | 0.8263 | 21.939 | 85.3829 | 21.12 | 5.24 | 6 | HAUL ROAD | 15.1665 | 4957
45645 | 0.82632 | 21.9389 | 85.3828 | 52.48 | 26.31 | 6 | HAUL ROAD | 15.1665 | 4958
45645 | 0.82634 | 21.9388 | 85.3827 | 63.36 | 23.79 | 6 | HAUL ROAD | 15.1668 | 4959
45645 | 0.82637 | 21.9388 | 85.3826 | 52.48 | 10.12 | 6 | HAUL ROAD | 10.3139 | 4960
45645 | 0.82639 | 21.9387 | 85.3825 | 49.76 | 10.12 | 6 | HAUL ROAD | 15.1665 | 4961
45645 | 0.82641 | 21.9386 | 85.3824 | 52.48 | 10.12 | 6 | HAUL ROAD | 15.1668 | 4962
45645 | 0.82644 | 21.9386 | 85.3823 | 74.25 | 26.31 | 6 | HAUL ROAD | 10.3148 | 4963
45645 | 0.82646 | 21.9385 | 85.3822 | 33.45 | 7.58 | 6 | HAUL ROAD | 15.1671 | 4964
45645 | 0.82648 | 21.9384 | 85.3821 | 49.76 | 3.16 | 6 | HAUL ROAD | 15.1668 | 4965
45645 | 0.8265 | 21.9383 | 85.382 | 36.16 | 30.73 | 6 | HAUL ROAD | 15.1665 | 4966
45645 | 0.82653 | 21.9382 | 85.3819 | 52.48 | 10.12 | 6 | HAUL ROAD | 15.1665 | 4967
45645 | 0.82655 | 21.9381 | 85.3818 | 93.32 | 30.73 | 6 | HAUL ROAD | 15.1668 | 4968
45645 | 0.82657 | 21.938 | 85.3817 | 18.36 | 15.57 | 6 | HAUL ROAD | 15.1668 | 4969
45645 | 0.8266 | 21.9379 | 85.3816 | 30.73 | 21.12 | 6 | HAUL ROAD | 15.1668 | 4970
45645 | 0.82662 | 21.9379 | 85.3815 | 52.48 | 7.58 | 6 | HAUL ROAD | 10.3144 | 4971
45645 | 0.82664 | 21.9378 | 85.3814 | 1.39 | 5.24 | 6 | HAUL ROAD | 15.1665 | 4972
45645 | 0.82667 | 21.9377 | 85.3814 | 44.32 | 1.39 | 6 | HAUL ROAD | 11.1196 | 4973
45645 | 0.82669 | 21.9376 | 85.3813 | 23.79 | 3.16 | 6 | HAUL ROAD | 15.1668 | 4974
45645 | 0.82671 | 21.9375 | 85.3812 | 49.76 | 0 | 6 | HAUL ROAD | 15.1671 | 4975
45645 | 0.82674 | 21.9374 | 85.3811 | 5.24 | 1.39 | 6 | HAUL ROAD | 15.1671 | 4976
45645 | 0.82676 | 21.9373 | 85.381 | 5.24 | 3.16 | 6 | HAUL ROAD | 15.1668 | 4977
45645 | 0.82678 | 21.9372 | 85.381 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 4978
45645 | 0.82681 | 21.9371 | 85.3809 | 10.12 | 7.58 | 6 | HAUL ROAD | 15.1668 | 4979
45645 | 0.82683 | 21.937 | 85.3808 | 10.12 | 3.16 | 6 | HAUL ROAD | 15.1668 | 4980
45645 | 0.82685 | 21.9369 | 85.3807 | 12.8 | 10.12 | 6 | HAUL ROAD | 15.1665 | 4981
45645 | 0.82688 | 21.9368 | 85.3806 | 23.79 | 1.39 | 6 | HAUL ROAD | 15.1665 | 4982
45645 | 0.8269 | 21.9367 | 85.3806 | 7.58 | 5.24 | 6 | HAUL ROAD | 11.1192 | 4983
45645 | 0.82692 | 21.9366 | 85.3805 | 26.31 | 0 | 6 | HAUL ROAD | 15.1668 | 4984
45645 | 0.82694 | 21.9365 | 85.3804 | 0 | 1.39 | 6 | HAUL ROAD | 15.1668 | 4985
45645 | 0.82697 | 21.9365 | 85.3803 | 0 | 0 | 6 | HAUL ROAD | 10.3144 | 4986
45645 | 0.82699 | 21.9364 | 85.3803 | 0 | 3.16 | 6 | HAUL ROAD | 11.1196 | 4987
45645 | 0.82701 | 21.9363 | 85.3802 | 0 | 3.16 | 6 | HAUL ROAD | 15.1668 | 4988
45645 | 0.82704 | 21.9362 | 85.3801 | 7.58 | 10.12 | 6 | HAUL ROAD | 15.1665 | 4989
45645 | 0.82706 | 21.9361 | 85.3801 | 21.12 | 21.12 | 6 | HAUL ROAD | 11.1192 | 4990
45645 | 0.82708 | 21.936 | 85.3801 | 55.2 | 26.31 | 6 | HAUL ROAD | 11.1196 | 4991
45645 | 0.82711 | 21.9359 | 85.3801 | 90.59 | 10.12 | 6 | HAUL ROAD | 11.1196 | 4992
45645 | 0.82713 | 21.9358 | 85.3801 | 101.5 | 10.12 | 6 | HAUL ROAD | 11.1192 | 4993
45645 | 0.82715 | 21.9357 | 85.3802 | 60.64 | 12.8 | 6 | HAUL ROAD | 15.1665 | 4994
45645 | 0.82718 | 21.9356 | 85.3802 | 36.16 | 1.39 | 6 | HAUL ROAD | 11.1196 | 4995
45645 | 0.8272 | 21.9355 | 85.3803 | 15.57 | 5.24 | 6 | HAUL ROAD | 15.1671 | 4996
45645 | 0.82722 | 21.9354 | 85.3803 | 21.12 | 12.8 | 6 | HAUL ROAD | 11.1196 | 4997
45645 | 0.82725 | 21.9353 | 85.3804 | 15.57 | 10.12 | 6 | HAUL ROAD | 15.1671 | 4998
45645 | 0.82727 | 21.9352 | 85.3804 | 10.12 | 44.32 | 6 | HAUL ROAD | 11.1192 | 4999
45645 | 0.82729 | 21.9352 | 85.3805 | 47.04 | 47.04 | 6 | HAUL ROAD | 10.3148 | 5000
45645 | 0.82731 | 21.9351 | 85.3806 | 57.92 | 52.48 | 6 | HAUL ROAD | 15.1668 | 5001
45645 | 0.82734 | 21.9351 | 85.3807 | 5.24 | 3.16 | 6 | HAUL ROAD | 10.3144 | 5002
45645 | 0.82736 | 21.9351 | 85.3808 | 0 | 5.24 | 6 | HAUL ROAD | 10.3144 | 5003
45645 | 0.82738 | 21.935 | 85.3809 | 10.12 | 5.24 | 6 | HAUL ROAD | 15.1668 | 5004
45645 | 0.82741 | 21.935 | 85.3811 | 7.58 | 0 | 6 | HAUL ROAD | 20.6292 | 5005
45645 | 0.82743 | 21.935 | 85.3812 | 0 | 0 | 6 | HAUL ROAD | 10.3148 | 5006
45645 | 0.82745 | 21.9351 | 85.3813 | 0 | 0 | 6 | HAUL ROAD | 15.1668 | 5007
45645 | 0.82748 | 21.9351 | 85.3814 | 1.39 | 0 | 6 | HAUL ROAD | 10.3144 | 5008
45645 | 0.8275 | 21.9351 | 85.3815 | 0 | 0 | 6 | HAUL ROAD | 10.3144 | 5009
45645 | 0.82752 | 21.935 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 15.1668 | 5010
45645 | 0.82755 | 21.935 | 85.3817 | 0 | 0 | 6 | HAUL ROAD | 10.3148 | 5011
45645 | 0.82757 | 21.9349 | 85.3818 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 5012
45645 | 0.82759 | 21.9348 | 85.3818 | 1.39 | 0 | 6 | HAUL ROAD | 11.12 | 5013
45645 | 0.82762 | 21.9347 | 85.3817 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 5014
45645 | 0.82764 | 21.9346 | 85.3817 | 0 | 0 | 6 | HAUL ROAD | 11.1192 | 5015
45645 | 0.82766 | 21.9345 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 5016
45645 | 0.82769 | 21.9344 | 85.3815 | 3.16 | 3.16 | 6 | HAUL ROAD | 15.1671 | 5017
45645 | 0.82771 | 21.9344 | 85.3814 | 10.12 | 0 | 6 | HAUL ROAD | 10.3152 | 5018
45645 | 0.82773 | 21.9343 | 85.3813 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 5019
45645 | 0.82775 | 21.9342 | 85.3813 | 5.24 | 1.39 | 6 | HAUL ROAD | 11.1192 | 5020
45645 | 0.82778 | 21.9341 | 85.3812 | 7.58 | 0 | 6 | HAUL ROAD | 15.1671 | 5021
45645 | 0.8278 | 21.934 | 85.3811 | 1.39 | 1.39 | 6 | HAUL ROAD | 15.1668 | 5022
45645 | 0.82782 | 21.934 | 85.381 | 1.39 | 1.39 | 6 | HAUL ROAD | 10.3148 | 5023
45645 | 0.82785 | 21.9339 | 85.381 | 3.16 | 3.16 | 6 | HAUL ROAD | 11.1196 | 5024
45645 | 0.82787 | 21.9338 | 85.3809 | 0 | 0 | 6 | HAUL ROAD | 15.1668 | 5025
45645 | 0.82789 | 21.9338 | 85.3808 | 0 | 3.16 | 6 | HAUL ROAD | 10.3148 | 5026
45645 | 0.82792 | 21.9337 | 85.3808 | 10.12 | 0 | 6 | HAUL ROAD | 11.1196 | 5027
45645 | 0.82794 | 21.9336 | 85.3807 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 5028
45645 | 0.82796 | 21.9336 | 85.3806 | 0 | 1.39 | 6 | HAUL ROAD | 10.3148 | 5029
45645 | 0.82799 | 21.9335 | 85.3806 | 5.24 | 5.24 | 6 | HAUL ROAD | 11.1192 | 5030
45645 | 0.82801 | 21.9335 | 85.3805 | 7.58 | 0 | 6 | HAUL ROAD | 10.3144 | 5031
45645 | 0.82803 | 21.9334 | 85.3804 | 1.39 | 0 | 6 | HAUL ROAD | 15.1668 | 5032
45645 | 0.82806 | 21.9333 | 85.3804 | 0 | 3.16 | 6 | HAUL ROAD | 11.1196 | 5033
45645 | 0.82808 | 21.9333 | 85.3803 | 10.12 | 0 | 6 | HAUL ROAD | 10.3144 | 5034
45645 | 0.8281 | 21.9332 | 85.3802 | 0 | 1.39 | 6 | HAUL ROAD | 15.1671 | 5035
45645 | 0.82812 | 21.9331 | 85.3802 | 1.39 | 5.24 | 6 | HAUL ROAD | 11.1196 | 5036
45645 | 0.82815 | 21.933 | 85.3801 | 7.58 | 0 | 6 | HAUL ROAD | 15.1671 | 5037
45645 | 0.82817 | 21.933 | 85.38 | 0 | 1.39 | 6 | HAUL ROAD | 10.3152 | 5038
45645 | 0.82819 | 21.9329 | 85.38 | 0 | 5.24 | 6 | HAUL ROAD | 11.1196 | 5039
45645 | 0.82822 | 21.9328 | 85.3799 | 10.12 | 1.39 | 6 | HAUL ROAD | 15.1671 | 5040
45645 | 0.82824 | 21.9327 | 85.3798 | 1.39 | 3.16 | 6 | HAUL ROAD | 15.1668 | 5041
45645 | 0.82826 | 21.9326 | 85.3798 | 0 | 7.58 | 6 | HAUL ROAD | 11.1192 | 5042
45645 | 0.82829 | 21.9325 | 85.3798 | 21.12 | 12.8 | 6 | HAUL ROAD | 11.1196 | 5043
45645 | 0.82831 | 21.9325 | 85.3797 | 18.36 | 10.12 | 6 | HAUL ROAD | 10.3152 | 5044
45645 | 0.82833 | 21.9324 | 85.3797 | 15.57 | 23.79 | 6 | HAUL ROAD | 11.1196 | 5045
45645 | 0.82836 | 21.9323 | 85.3797 | 60.64 | 33.45 | 6 | HAUL ROAD | 11.1196 | 5046
45645 | 0.82838 | 21.9322 | 85.3797 | 66.08 | 10.12 | 6 | HAUL ROAD | 11.12 | 5047
45645 | 0.8284 | 21.9321 | 85.3797 | 33.45 | 12.8 | 6 | HAUL ROAD | 11.1196 | 5048
45645 | 0.82843 | 21.9321 | 85.3797 | 10.12 | 12.8 | 6 | HAUL ROAD | 0.094935 | 5049
45645 | 0.82845 | 21.932 | 85.3797 | 7.58 | 12.8 | 6 | HAUL ROAD | 11.1196 | 5050
45645 | 0.82847 | 21.9321 | 85.3798 | 7.58 | 7.58 | 6 | HAUL ROAD | 15.1671 | 5051
45645 | 0.8285 | 21.9321 | 85.3799 | 10.12 | 10.12 | 6 | HAUL ROAD | 10.3152 | 5052
45645 | 0.82852 | 21.9322 | 85.38 | 44.32 | 1.39 | 6 | HAUL ROAD | 15.1671 | 5053
45645 | 0.82854 | 21.9322 | 85.3801 | 41.6 | 3.16 | 6 | HAUL ROAD | 10.3152 | 5054
45645 | 0.82856 | 21.9322 | 85.3802 | 3.16 | 1.39 | 6 | HAUL ROAD | 10.3152 | 5055
45645 | 0.82859 | 21.9322 | 85.3803 | 0 | 0 | 6 | HAUL ROAD | 10.3152 | 5056
45645 | 0.82861 | 21.9321 | 85.3804 | 7.58 | 0 | 6 | HAUL ROAD | 15.1671 | 5057
45645 | 0.82863 | 21.932 | 85.3805 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 5058
45645 | 0.82866 | 21.932 | 85.3806 | 5.24 | 0 | 6 | HAUL ROAD | 10.3148 | 5059
45645 | 0.82868 | 21.9319 | 85.3807 | 0 | 5.24 | 6 | HAUL ROAD | 15.1671 | 5060
45645 | 0.8287 | 21.9319 | 85.3808 | 10.12 | 0 | 6 | HAUL ROAD | 10.3152 | 5061
45645 | 0.82873 | 21.9319 | 85.3809 | 0 | 1.39 | 6 | HAUL ROAD | 10.3152 | 5062
45645 | 0.82875 | 21.9318 | 85.381 | 1.39 | 12.8 | 6 | HAUL ROAD | 15.1671 | 5063
45645 | 0.82877 | 21.9318 | 85.3811 | 12.8 | 30.73 | 6 | HAUL ROAD | 10.3148 | 5064
45645 | 0.8288 | 21.9318 | 85.3812 | 74.25 | 49.76 | 6 | HAUL ROAD | 10.3148 | 5065
45645 | 0.82882 | 21.9317 | 85.3812 | 112.41 | 10.12 | 6 | HAUL ROAD | 11.1196 | 5066
45645 | 0.82884 | 21.9317 | 85.3813 | 30.73 | 23.79 | 6 | HAUL ROAD | 10.3148 | 5067
45645 | 0.82887 | 21.9316 | 85.3813 | 5.24 | 0 | 6 | HAUL ROAD | 11.1196 | 5068
45645 | 0.82889 | 21.9315 | 85.3814 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 5069
45645 | 0.82891 | 21.9315 | 85.3814 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5070
45645 | 0.82894 | 21.9314 | 85.3814 | 0 | 15.57 | 6 | HAUL ROAD | 11.12 | 5071
45645 | 0.82896 | 21.9314 | 85.3815 | 5.24 | 23.79 | 6 | HAUL ROAD | 10.3152 | 5072
45645 | 0.82898 | 21.9313 | 85.3815 | 21.12 | 44.32 | 6 | HAUL ROAD | 11.1196 | 5073
45645 | 0.829 | 21.9313 | 85.3815 | 71.53 | 33.45 | 6 | HAUL ROAD | 0 | 5074
45645 | 0.82903 | 21.9312 | 85.3815 | 55.2 | 1.39 | 6 | HAUL ROAD | 11.1196 | 5075
45645 | 0.82905 | 21.9312 | 85.3816 | 10.12 | 0 | 6 | HAUL ROAD | 10.3144 | 5076
45645 | 0.82907 | 21.9312 | 85.3816 | 5.24 | 10.12 | 6 | HAUL ROAD | 0 | 5077
45645 | 0.8291 | 21.9312 | 85.3816 | 5.24 | 23.79 | 6 | HAUL ROAD | 0 | 5078
45645 | 0.82912 | 21.9312 | 85.3816 | 18.36 | 44.32 | 6 | HAUL ROAD | 0 | 5079
45645 | 0.82914 | 21.9312 | 85.3816 | 30.73 | 57.92 | 6 | HAUL ROAD | 0 | 5080
45645 | 0.82917 | 21.9312 | 85.3816 | 44.32 | 66.08 | 6 | HAUL ROAD | 0 | 5081
45645 | 0.82919 | 21.9312 | 85.3816 | 44.32 | 68.8 | 6 | HAUL ROAD | 0 | 5082
45645 | 0.82921 | 21.9312 | 85.3816 | 47.04 | 68.8 | 6 | HAUL ROAD | 0 | 5083
45645 | 0.82924 | 21.9312 | 85.3816 | 44.32 | 71.53 | 6 | HAUL ROAD | 0 | 5084
45645 | 0.82926 | 21.9312 | 85.3816 | 44.32 | 68.8 | 6 | HAUL ROAD | 0 | 5085
45645 | 0.82928 | 21.9312 | 85.3816 | 44.32 | 68.8 | 6 | HAUL ROAD | 0 | 5086
45645 | 0.82931 | 21.9312 | 85.3816 | 44.32 | 68.8 | 6 | HAUL ROAD | 0 | 5087
45645 | 0.82933 | 21.9312 | 85.3816 | 44.32 | 71.53 | 6 | HAUL ROAD | 0 | 5088
45645 | 0.82935 | 21.9312 | 85.3816 | 44.32 | 68.8 | 6 | HAUL ROAD | 0 | 5089
45645 | 0.82937 | 21.9312 | 85.3816 | 44.32 | 68.8 | 6 | HAUL ROAD | 0 | 5090
45645 | 0.8294 | 21.9312 | 85.3817 | 44.32 | 68.8 | 6 | HAUL ROAD | 10.3144 | 5091
45645 | 0.82942 | 21.9312 | 85.3817 | 44.32 | 68.8 | 6 | HAUL ROAD | 0 | 5092
45645 | 0.82944 | 21.9312 | 85.3817 | 44.32 | 68.8 | 6 | HAUL ROAD | 0 | 5093
45645 | 0.82947 | 21.9312 | 85.3817 | 44.32 | 68.8 | 6 | HAUL ROAD | 0 | 5094
45645 | 0.82949 | 21.9312 | 85.3817 | 44.32 | 68.8 | 6 | HAUL ROAD | 0 | 5095
45645 | 0.82951 | 21.9312 | 85.3817 | 47.04 | 68.8 | 6 | HAUL ROAD | 0 | 5096
45645 | 0.82954 | 21.9312 | 85.3817 | 44.32 | 71.53 | 6 | HAUL ROAD | 0 | 5097
45645 | 0.82956 | 21.9312 | 85.3817 | 44.32 | 71.53 | 6 | HAUL ROAD | 0 | 5098
45645 | 0.82958 | 21.9312 | 85.3817 | 47.04 | 68.8 | 6 | HAUL ROAD | 0 | 5099
45645 | 0.82961 | 21.9312 | 85.3817 | 49.76 | 68.8 | 6 | HAUL ROAD | 0 | 5100
45645 | 0.82963 | 21.9312 | 85.3817 | 55.2 | 74.25 | 6 | HAUL ROAD | 0 | 5101
45645 | 0.82965 | 21.9312 | 85.3817 | 90.59 | 93.32 | 6 | HAUL ROAD | 0 | 5102
45645 | 0.82968 | 21.9312 | 85.3817 | 156.12 | 98.77 | 6 | HAUL ROAD | 0 | 5103
45645 | 0.8297 | 21.9312 | 85.3817 | 169.8 | 5.24 | 6 | HAUL ROAD | 0 | 5104
45645 | 0.82972 | 21.9312 | 85.3817 | 98.77 | 0 | 6 | HAUL ROAD | 0 | 5105
45645 | 0.82975 | 21.9312 | 85.3817 | 41.6 | 1.39 | 6 | HAUL ROAD | 0 | 5106
45645 | 0.82977 | 21.9312 | 85.3818 | 15.57 | 1.39 | 13.3 | DIESEL PUMP AREA | 10.3144 | 5107
45645 | 0.82979 | 21.9312 | 85.3818 | 0 | 0 | 6 | HAUL ROAD | 0 | 5108
45645 | 0.82981 | 21.9311 | 85.3818 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 5109
45645 | 0.82984 | 21.9311 | 85.3818 | 0 | 0 | 6 | HAUL ROAD | 0 | 5110
45645 | 0.82986 | 21.9311 | 85.3818 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 5111
45645 | 0.82988 | 21.9311 | 85.3819 | 0 | 1.39 | 6 | HAUL ROAD | 10.3152 | 5112
45645 | 0.82991 | 21.9311 | 85.3819 | 1.39 | 1.39 | 6 | HAUL ROAD | 0 | 5113
45645 | 0.82993 | 21.9312 | 85.3819 | 3.16 | 0 | 13.3 | DIESEL PUMP AREA | 11.1196 | 5114
45645 | 0.82995 | 21.9312 | 85.3819 | 12.8 | 0 | 13.3 | DIESEL PUMP AREA | 0 | 5115
45645 | 0.82998 | 21.9312 | 85.3819 | 3.16 | 0 | 13.3 | DIESEL PUMP AREA | 0 | 5116
45645 | 0.83 | 21.9312 | 85.3819 | 0 | 7.58 | 13.3 | DIESEL PUMP AREA | 0 | 5117
45645 | 0.83002 | 21.9312 | 85.3819 | 0 | 15.57 | 13.3 | DIESEL PUMP AREA | 0 | 5118
45645 | 0.83005 | 21.9312 | 85.3819 | 3.16 | 18.36 | 13.3 | DIESEL PUMP AREA | 0 | 5119
45645 | 0.83007 | 21.9312 | 85.3819 | 3.16 | 33.45 | 13.3 | DIESEL PUMP AREA | 0 | 5120
45645 | 0.83009 | 21.9313 | 85.3818 | 5.24 | 33.45 | 13.3 | DIESEL PUMP AREA | 15.1671 | 5121
45645 | 0.83012 | 21.9313 | 85.3818 | 12.8 | 38.88 | 13.3 | DIESEL PUMP AREA | 0 | 5122
45645 | 0.83014 | 21.9313 | 85.3818 | 23.79 | 63.36 | 13.3 | DIESEL PUMP AREA | 0 | 5123
45645 | 0.83016 | 21.9313 | 85.3818 | 49.76 | 87.87 | 13.3 | DIESEL PUMP AREA | 0 | 5124
45645 | 0.83019 | 21.9313 | 85.3818 | 79.7 | 96.05 | 13.3 | DIESEL PUMP AREA | 0 | 5125
45645 | 0.83021 | 21.9313 | 85.3818 | 96.05 | 26.31 | 13.3 | DIESEL PUMP AREA | 0 | 5126
45645 | 0.83023 | 21.9313 | 85.3817 | 44.32 | 0 | 6 | HAUL ROAD | 10.3148 | 5127
45645 | 0.83025 | 21.9313 | 85.3817 | 7.58 | 10.12 | 6 | HAUL ROAD | 0 | 5128
45645 | 0.83028 | 21.9312 | 85.3817 | 7.58 | 23.79 | 6 | HAUL ROAD | 11.1196 | 5129
45645 | 0.8303 | 21.9312 | 85.3817 | 12.8 | 26.31 | 6 | HAUL ROAD | 0 | 5130
45645 | 0.83032 | 21.9312 | 85.3817 | 12.8 | 26.31 | 6 | HAUL ROAD | 0 | 5131
45645 | 0.83035 | 21.9312 | 85.3817 | 21.12 | 41.6 | 6 | HAUL ROAD | 0 | 5132
45645 | 0.83037 | 21.9311 | 85.3817 | 82.42 | 74.25 | 6 | HAUL ROAD | 11.1196 | 5133
45645 | 0.83039 | 21.9311 | 85.3817 | 128.79 | 1.39 | 6 | HAUL ROAD | 0 | 5134
45645 | 0.83042 | 21.9311 | 85.3817 | 85.14 | 0 | 6 | HAUL ROAD | 0 | 5135
45645 | 0.83044 | 21.9311 | 85.3816 | 15.57 | 0 | 6 | HAUL ROAD | 10.3152 | 5136
45645 | 0.83046 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 5137
45645 | 0.83049 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5138
45645 | 0.83051 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5139
45645 | 0.83053 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5140
45645 | 0.83056 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5141
45645 | 0.83058 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5142
45645 | 0.8306 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5143
45645 | 0.83062 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5144
45645 | 0.83065 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5145
45645 | 0.83067 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5146
45645 | 0.83069 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5147
45645 | 0.83072 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5148
45645 | 0.83074 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5149
45645 | 0.83076 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5150
45645 | 0.83079 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5151
45645 | 0.83081 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5152
45645 | 0.83083 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5153
45645 | 0.83086 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5154
45645 | 0.83088 | 21.9312 | 85.3816 | 0 | 0 | 6 | HAUL ROAD | 0 | 5155
45645 | 0.8309 | 21.9312 | 85.3816 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 5156
45645 | 0.83093 | 21.9313 | 85.3816 | 18.36 | 1.39 | 6 | HAUL ROAD | 11.1196 | 5157
45645 | 0.83095 | 21.9313 | 85.3815 | 79.7 | 0 | 6 | HAUL ROAD | 10.3148 | 5158
45645 | 0.83097 | 21.9314 | 85.3815 | 57.92 | 0 | 6 | HAUL ROAD | 11.1196 | 5159
45645 | 0.831 | 21.9314 | 85.3815 | 3.16 | 0 | 6 | HAUL ROAD | 0.094935 | 5160
45645 | 0.83102 | 21.9314 | 85.3814 | 0 | 0 | 6 | HAUL ROAD | 10.3152 | 5161
45645 | 0.83104 | 21.9315 | 85.3814 | 0 | 0 | 6 | HAUL ROAD | 11.12 | 5162
45645 | 0.83106 | 21.9315 | 85.3814 | 0 | 0 | 6 | HAUL ROAD | 0 | 5163
45645 | 0.83109 | 21.9316 | 85.3813 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 5164
45645 | 0.83111 | 21.9316 | 85.3813 | 0 | 0 | 6 | HAUL ROAD | 0 | 5165
45645 | 0.83113 | 21.9317 | 85.3813 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 5166
45645 | 0.83116 | 21.9317 | 85.3812 | 21.12 | 0 | 6 | HAUL ROAD | 10.3148 | 5167
45645 | 0.83118 | 21.9317 | 85.3812 | 5.24 | 3.16 | 6 | HAUL ROAD | 0 | 5168
45645 | 0.8312 | 21.9317 | 85.3811 | 126.06 | 0 | 6 | HAUL ROAD | 10.3148 | 5169
45645 | 0.83123 | 21.9317 | 85.3811 | 112.41 | 3.16 | 6 | HAUL ROAD | 0 | 5170
45645 | 0.83125 | 21.9317 | 85.3811 | 47.04 | 1.39 | 6 | HAUL ROAD | 0 | 5171
45645 | 0.83127 | 21.9316 | 85.3811 | 7.58 | 15.57 | 6 | HAUL ROAD | 11.1196 | 5172
45645 | 0.8313 | 21.9315 | 85.3811 | 44.32 | 21.12 | 6 | HAUL ROAD | 11.1192 | 5173
45645 | 0.83132 | 21.9315 | 85.3812 | 52.48 | 33.45 | 6 | HAUL ROAD | 10.3148 | 5174
45645 | 0.83134 | 21.9314 | 85.3812 | 150.65 | 18.36 | 6 | HAUL ROAD | 11.12 | 5175
45645 | 0.83137 | 21.9313 | 85.3813 | 63.36 | 82.42 | 4 | S5 | 15.1671 | 5176
45645 | 0.83139 | 21.9312 | 85.3814 | 147.92 | 18.36 | 6 | HAUL ROAD | 15.1671 | 5177
45645 | 0.83141 | 21.9311 | 85.3814 | 66.08 | 96.05 | 4 | S4 | 11.1196 | 5178
45645 | 0.83144 | 21.931 | 85.3815 | 90.59 | 3.16 | 6 | HAUL ROAD | 15.1671 | 5179
45645 | 0.83146 | 21.9309 | 85.3815 | 82.42 | 38.88 | 6 | HAUL ROAD | 11.12 | 5180
45645 | 0.83148 | 21.9308 | 85.3815 | 36.16 | 57.92 | 6 | HAUL ROAD | 11.12 | 5181
45645 | 0.8315 | 21.9307 | 85.3816 | 147.92 | 15.57 | 6 | HAUL ROAD | 15.1671 | 5182
45645 | 0.83153 | 21.9306 | 85.3816 | 33.45 | 52.48 | 6 | HAUL ROAD | 11.1192 | 5183
45645 | 0.83155 | 21.9305 | 85.3817 | 74.25 | 0 | 6 | HAUL ROAD | 15.1671 | 5184
45645 | 0.83157 | 21.9304 | 85.3817 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 5185
45645 | 0.8316 | 21.9304 | 85.3818 | 0 | 0 | 6 | HAUL ROAD | 10.3148 | 5186
45645 | 0.83162 | 21.9303 | 85.3819 | 1.39 | 0 | 6 | HAUL ROAD | 15.1671 | 5187
45645 | 0.83164 | 21.9302 | 85.3819 | 0 | 1.39 | 6 | HAUL ROAD | 11.1192 | 5188
45645 | 0.83167 | 21.9302 | 85.382 | 0 | 1.39 | 6 | HAUL ROAD | 10.3148 | 5189
45645 | 0.83169 | 21.9301 | 85.382 | 1.39 | 3.16 | 6 | HAUL ROAD | 11.1196 | 5190
45645 | 0.83171 | 21.9301 | 85.3821 | 0 | 5.24 | 6 | HAUL ROAD | 10.3152 | 5191
45645 | 0.83174 | 21.93 | 85.3822 | 1.39 | 3.16 | 6 | HAUL ROAD | 15.1671 | 5192
45645 | 0.83176 | 21.93 | 85.3822 | 5.24 | 1.39 | 6 | HAUL ROAD | 0.094935 | 5193
45645 | 0.83178 | 21.9299 | 85.3822 | 3.16 | 1.39 | 6 | HAUL ROAD | 11.1196 | 5194
45645 | 0.83181 | 21.9299 | 85.3823 | 3.16 | 3.16 | 6 | HAUL ROAD | 10.3152 | 5195
45645 | 0.83183 | 21.9298 | 85.3823 | 7.58 | 5.24 | 6 | HAUL ROAD | 11.12 | 5196
45645 | 0.83185 | 21.9298 | 85.3824 | 5.24 | 5.24 | 6 | HAUL ROAD | 10.3152 | 5197
45645 | 0.83188 | 21.9298 | 85.3824 | 7.58 | 1.39 | 6 | HAUL ROAD | 0.094935 | 5198
45645 | 0.8319 | 21.9298 | 85.3825 | 10.12 | 3.16 | 6 | HAUL ROAD | 10.3152 | 5199
45645 | 0.83192 | 21.9298 | 85.3826 | 52.48 | 23.79 | 6 | HAUL ROAD | 10.3152 | 5200
45645 | 0.83194 | 21.9299 | 85.3827 | 230.12 | 55.2 | 6 | HAUL ROAD | 15.1671 | 5201
45645 | 0.83197 | 21.9299 | 85.3828 | 169.8 | 30.73 | 6 | HAUL ROAD | 10.3152 | 5202
45645 | 0.83199 | 21.93 | 85.3829 | 79.7 | 26.31 | 6 | HAUL ROAD | 15.1671 | 5203
45645 | 0.83201 | 21.93 | 85.383 | 169.8 | 0 | 6 | HAUL ROAD | 10.3152 | 5204
45645 | 0.83204 | 21.93 | 85.3831 | 66.08 | 10.12 | 6 | HAUL ROAD | 10.3152 | 5205
45645 | 0.83206 | 21.9301 | 85.3832 | 49.76 | 1.39 | 6 | HAUL ROAD | 15.1671 | 5206
45645 | 0.83208 | 21.9301 | 85.3833 | 3.16 | 3.16 | 6 | HAUL ROAD | 10.3152 | 5207
45645 | 0.83211 | 21.9301 | 85.3834 | 10.12 | 5.24 | 6 | HAUL ROAD | 10.3152 | 5208
45645 | 0.83213 | 21.9301 | 85.3835 | 10.12 | 5.24 | 6 | HAUL ROAD | 10.3152 | 5209
45645 | 0.83215 | 21.9302 | 85.3836 | 0 | 10.12 | 6 | HAUL ROAD | 15.1671 | 5210
45645 | 0.83218 | 21.9302 | 85.3836 | 7.58 | 3.16 | 6 | HAUL ROAD | 0 | 5211
45645 | 0.8322 | 21.9302 | 85.3837 | 5.24 | 1.39 | 6 | HAUL ROAD | 10.3148 | 5212
45645 | 0.83222 | 21.9302 | 85.3838 | 12.8 | 18.36 | 6 | HAUL ROAD | 10.3148 | 5213
45645 | 0.83225 | 21.9302 | 85.3839 | 76.97 | 5.24 | 6 | HAUL ROAD | 10.3148 | 5214
45645 | 0.83227 | 21.9303 | 85.384 | 41.6 | 1.39 | 6 | HAUL ROAD | 15.1671 | 5215
45645 | 0.83229 | 21.9303 | 85.3841 | 3.16 | 5.24 | 6 | HAUL ROAD | 10.3144 | 5216
45645 | 0.83231 | 21.9303 | 85.3842 | 10.12 | 10.12 | 6 | HAUL ROAD | 10.3144 | 5217
45645 | 0.83234 | 21.9303 | 85.3842 | 12.8 | 15.57 | 6 | HAUL ROAD | 0 | 5218
45645 | 0.83236 | 21.9303 | 85.3842 | 7.58 | 18.36 | 6 | HAUL ROAD | 0 | 5219
45645 | 0.83238 | 21.9303 | 85.3843 | 7.58 | 26.31 | 6 | HAUL ROAD | 10.3144 | 5220
45645 | 0.83241 | 21.9303 | 85.3843 | 3.16 | 18.36 | 6 | HAUL ROAD | 0 | 5221
45645 | 0.83243 | 21.9303 | 85.3843 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 5222
45645 | 0.83245 | 21.9303 | 85.3843 | 1.39 | 10.12 | 6 | HAUL ROAD | 0 | 5223
45645 | 0.83248 | 21.9303 | 85.3843 | 1.39 | 10.12 | 6 | HAUL ROAD | 0 | 5224
45645 | 0.8325 | 21.9303 | 85.3843 | 1.39 | 10.12 | 6 | HAUL ROAD | 0 | 5225
45645 | 0.83252 | 21.9303 | 85.3843 | 1.39 | 10.12 | 6 | HAUL ROAD | 0 | 5226
45645 | 0.83255 | 21.9303 | 85.3843 | 1.39 | 10.12 | 6 | HAUL ROAD | 0 | 5227
45645 | 0.83257 | 21.9303 | 85.3843 | 1.39 | 10.12 | 6 | HAUL ROAD | 0 | 5228
45645 | 0.83259 | 21.9303 | 85.3843 | 1.39 | 10.12 | 6 | HAUL ROAD | 0 | 5229
45645 | 0.83262 | 21.9303 | 85.3843 | 1.39 | 10.12 | 6 | HAUL ROAD | 0 | 5230
45645 | 0.83264 | 21.9303 | 85.3843 | 1.39 | 10.12 | 6 | HAUL ROAD | 0 | 5231
45645 | 0.83266 | 21.9303 | 85.3844 | 1.39 | 10.12 | 6 | HAUL ROAD | 10.3144 | 5232
45645 | 0.83269 | 21.9302 | 85.3844 | 7.58 | 10.12 | 6 | HAUL ROAD | 11.1192 | 5233
45645 | 0.83271 | 21.9302 | 85.3845 | 60.64 | 3.16 | 6 | HAUL ROAD | 10.3148 | 5234
45645 | 0.83273 | 21.9302 | 85.3845 | 7.58 | 1.39 | 6 | HAUL ROAD | 0 | 5235
45645 | 0.83275 | 21.9302 | 85.3845 | 0 | 1.39 | 6 | HAUL ROAD | 0 | 5236
45645 | 0.83278 | 21.9301 | 85.3846 | 7.58 | 3.16 | 6 | HAUL ROAD | 15.1671 | 5237
45645 | 0.8328 | 21.9301 | 85.3845 | 5.24 | 1.39 | 6 | HAUL ROAD | 10.3152 | 5238
45645 | 0.83282 | 21.9301 | 85.3845 | 1.39 | 7.58 | 6 | HAUL ROAD | 0 | 5239
45645 | 0.83285 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5240
45645 | 0.83287 | 21.9301 | 85.3845 | 0 | 0 | 6 | HAUL ROAD | 0 | 5241
45645 | 0.83289 | 21.9301 | 85.3845 | 1.39 | 3.16 | 6 | HAUL ROAD | 0 | 5242
45645 | 0.83292 | 21.9301 | 85.3845 | 1.39 | 3.16 | 6 | HAUL ROAD | 0 | 5243
45645 | 0.83294 | 21.9301 | 85.3845 | 0 | 0 | 6 | HAUL ROAD | 0 | 5244
45645 | 0.83296 | 21.9301 | 85.3845 | 1.39 | 18.36 | 6 | HAUL ROAD | 0 | 5245
45645 | 0.83299 | 21.9301 | 85.3845 | 1.39 | 18.36 | 6 | HAUL ROAD | 0 | 5246
45645 | 0.83301 | 21.9301 | 85.3845 | 3.16 | 10.12 | 6 | HAUL ROAD | 0 | 5247
45645 | 0.83303 | 21.9301 | 85.3845 | 1.39 | 12.8 | 6 | HAUL ROAD | 0 | 5248
45645 | 0.83306 | 21.9301 | 85.3845 | 1.39 | 10.12 | 6 | HAUL ROAD | 0 | 5249
45645 | 0.83308 | 21.9301 | 85.3845 | 1.39 | 10.12 | 6 | HAUL ROAD | 0 | 5250
45645 | 0.8331 | 21.9301 | 85.3845 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 5251
45645 | 0.83313 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5252
45645 | 0.83315 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5253
45645 | 0.83317 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5254
45645 | 0.83319 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5255
45645 | 0.83322 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5256
45645 | 0.83324 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5257
45645 | 0.83326 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5258
45645 | 0.83329 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5259
45645 | 0.83331 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5260
45645 | 0.83333 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5261
45645 | 0.83336 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5262
45645 | 0.83338 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5263
45645 | 0.8334 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5264
45645 | 0.83343 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5265
45645 | 0.83345 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5266
45645 | 0.83347 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5267
45645 | 0.8335 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5268
45645 | 0.83352 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5269
45645 | 0.83354 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5270
45645 | 0.83356 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5271
45645 | 0.83359 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5272
45645 | 0.83361 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5273
45645 | 0.83363 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5274
45645 | 0.83366 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5275
45645 | 0.83368 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5276
45645 | 0.8337 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5277
45645 | 0.83373 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5278
45645 | 0.83375 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5279
45645 | 0.83377 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5280
45645 | 0.8338 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5281
45645 | 0.83382 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5282
45645 | 0.83384 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5283
45645 | 0.83387 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5284
45645 | 0.83389 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5285
45645 | 0.83391 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5286
45645 | 0.83394 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5287
45645 | 0.83396 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5288
45645 | 0.83398 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5289
45645 | 0.834 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5290
45645 | 0.83403 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5291
45645 | 0.83405 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5292
45645 | 0.83407 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5293
45645 | 0.8341 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5294
45645 | 0.83412 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5295
45645 | 0.83414 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5296
45645 | 0.83417 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5297
45645 | 0.83419 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5298
45645 | 0.83421 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5299
45645 | 0.83424 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5300
45645 | 0.83426 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5301
45645 | 0.83428 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5302
45645 | 0.83431 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5303
45645 | 0.83433 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5304
45645 | 0.83435 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5305
45645 | 0.83437 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5306
45645 | 0.8344 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5307
45645 | 0.83442 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5308
45645 | 0.83444 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5309
45645 | 0.83447 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5310
45645 | 0.83449 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5311
45645 | 0.83451 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5312
45645 | 0.83454 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5313
45645 | 0.83456 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5314
45645 | 0.83458 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5315
45645 | 0.83461 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5316
45645 | 0.83463 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5317
45645 | 0.83465 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5318
45645 | 0.83468 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5319
45645 | 0.8347 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5320
45645 | 0.83472 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5321
45645 | 0.83475 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5322
45645 | 0.83477 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5323
45645 | 0.83479 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5324
45645 | 0.83481 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5325
45645 | 0.83484 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5326
45645 | 0.83486 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5327
45645 | 0.83488 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5328
45645 | 0.83491 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5329
45645 | 0.83493 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5330
45645 | 0.83495 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5331
45645 | 0.83498 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5332
45645 | 0.835 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5333
45645 | 0.83502 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5334
45645 | 0.83505 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5335
45645 | 0.83507 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5336
45645 | 0.83509 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5337
45645 | 0.83512 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5338
45645 | 0.83514 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5339
45645 | 0.83516 | 21.9301 | 85.3845 | 0 | 3.16 | 6 | HAUL ROAD | 0 | 5340
45645 | 0.83519 | 21.9301 | 85.3845 | 0 | 5.24 | 6 | HAUL ROAD | 0 | 5341
45645 | 0.83521 | 21.9302 | 85.3845 | 1.39 | 12.8 | 6 | HAUL ROAD | 11.1196 | 5342
45645 | 0.83523 | 21.9302 | 85.3845 | 3.16 | 18.36 | 6 | HAUL ROAD | 0 | 5343
45645 | 0.83525 | 21.9302 | 85.3845 | 3.16 | 15.57 | 6 | HAUL ROAD | 0 | 5344
45645 | 0.83528 | 21.9302 | 85.3845 | 3.16 | 18.36 | 6 | HAUL ROAD | 0 | 5345
45645 | 0.8353 | 21.9302 | 85.3845 | 3.16 | 15.57 | 6 | HAUL ROAD | 0 | 5346
45645 | 0.83532 | 21.9302 | 85.3845 | 3.16 | 15.57 | 6 | HAUL ROAD | 0 | 5347
45645 | 0.83535 | 21.9302 | 85.3845 | 3.16 | 15.57 | 6 | HAUL ROAD | 0 | 5348
45645 | 0.83537 | 21.9302 | 85.3845 | 3.16 | 18.36 | 6 | HAUL ROAD | 0 | 5349
45645 | 0.83539 | 21.9302 | 85.3844 | 7.58 | 26.31 | 6 | HAUL ROAD | 10.3148 | 5350
45645 | 0.83542 | 21.9302 | 85.3844 | 10.12 | 36.16 | 6 | HAUL ROAD | 0 | 5351
45645 | 0.83544 | 21.9302 | 85.3844 | 5.24 | 7.58 | 6 | HAUL ROAD | 0 | 5352
45645 | 0.83546 | 21.9302 | 85.3843 | 0 | 3.16 | 6 | HAUL ROAD | 10.3148 | 5353
45645 | 0.83549 | 21.9302 | 85.3842 | 1.39 | 5.24 | 6 | HAUL ROAD | 10.3148 | 5354
45645 | 0.83551 | 21.9302 | 85.3841 | 7.58 | 7.58 | 6 | HAUL ROAD | 10.3148 | 5355
45645 | 0.83553 | 21.9302 | 85.384 | 5.24 | 12.8 | 6 | HAUL ROAD | 10.3148 | 5356
45645 | 0.83556 | 21.9302 | 85.3839 | 30.73 | 26.31 | 6 | HAUL ROAD | 10.3148 | 5357
45645 | 0.83558 | 21.9302 | 85.3838 | 71.53 | 1.39 | 6 | HAUL ROAD | 10.3148 | 5358
45645 | 0.8356 | 21.9301 | 85.3837 | 26.31 | 1.39 | 6 | HAUL ROAD | 15.1671 | 5359
45645 | 0.83562 | 21.9301 | 85.3836 | 3.16 | 7.58 | 6 | HAUL ROAD | 10.3152 | 5360
45645 | 0.83565 | 21.9301 | 85.3835 | 10.12 | 5.24 | 6 | HAUL ROAD | 10.3152 | 5361
45645 | 0.83567 | 21.9301 | 85.3834 | 1.39 | 5.24 | 6 | HAUL ROAD | 10.3152 | 5362
45645 | 0.83569 | 21.93 | 85.3833 | 15.57 | 7.58 | 6 | HAUL ROAD | 15.1671 | 5363
45645 | 0.83572 | 21.93 | 85.3832 | 12.8 | 15.57 | 6 | HAUL ROAD | 10.3152 | 5364
45645 | 0.83574 | 21.93 | 85.3831 | 30.73 | 52.48 | 6 | HAUL ROAD | 10.3152 | 5365
45645 | 0.83576 | 21.93 | 85.383 | 90.59 | 82.42 | 6 | HAUL ROAD | 10.3152 | 5366
45645 | 0.83579 | 21.9299 | 85.3829 | 117.87 | 96.05 | 6 | HAUL ROAD | 15.1671 | 5367
45645 | 0.83581 | 21.9299 | 85.3828 | 249.35 | 44.32 | 6 | HAUL ROAD | 10.3152 | 5368
45645 | 0.83583 | 21.9298 | 85.3827 | 194.45 | 21.12 | 6 | HAUL ROAD | 15.1671 | 5369
45645 | 0.83586 | 21.9297 | 85.3827 | 150.65 | 44.32 | 6 | HAUL ROAD | 11.1196 | 5370
45645 | 0.83588 | 21.9297 | 85.3826 | 188.97 | 12.8 | 6 | HAUL ROAD | 10.3148 | 5371
45645 | 0.8359 | 21.9297 | 85.3825 | 41.6 | 12.8 | 6 | HAUL ROAD | 10.3148 | 5372
45645 | 0.83593 | 21.9297 | 85.3824 | 12.8 | 18.36 | 6 | HAUL ROAD | 10.3148 | 5373
45645 | 0.83595 | 21.9298 | 85.3824 | 5.24 | 15.57 | 6 | HAUL ROAD | 11.1196 | 5374
45645 | 0.83597 | 21.9298 | 85.3823 | 3.16 | 5.24 | 6 | HAUL ROAD | 10.3152 | 5375
45645 | 0.836 | 21.9299 | 85.3823 | 1.39 | 1.39 | 6 | HAUL ROAD | 11.12 | 5376
45645 | 0.83602 | 21.9299 | 85.3822 | 0 | 1.39 | 6 | HAUL ROAD | 10.3152 | 5377
45645 | 0.83604 | 21.93 | 85.3822 | 0 | 1.39 | 6 | HAUL ROAD | 11.1196 | 5378
45645 | 0.83606 | 21.93 | 85.3821 | 1.39 | 0 | 6 | HAUL ROAD | 10.3152 | 5379
45645 | 0.83609 | 21.9301 | 85.382 | 1.39 | 1.39 | 6 | HAUL ROAD | 15.1671 | 5380
45645 | 0.83611 | 21.9302 | 85.382 | 0 | 1.39 | 6 | HAUL ROAD | 11.1196 | 5381
45645 | 0.83613 | 21.9302 | 85.3819 | 1.39 | 0 | 6 | HAUL ROAD | 10.3148 | 5382
45645 | 0.83616 | 21.9303 | 85.3818 | 1.39 | 1.39 | 6 | HAUL ROAD | 15.1671 | 5383
45645 | 0.83618 | 21.9304 | 85.3818 | 0 | 1.39 | 6 | HAUL ROAD | 11.1192 | 5384
45645 | 0.8362 | 21.9305 | 85.3817 | 0 | 5.24 | 6 | HAUL ROAD | 15.1671 | 5385
45645 | 0.83623 | 21.9305 | 85.3817 | 0 | 3.16 | 6 | HAUL ROAD | 0.094935 | 5386
45645 | 0.83625 | 21.9306 | 85.3816 | 134.25 | 44.32 | 6 | HAUL ROAD | 15.1671 | 5387
45645 | 0.83627 | 21.9307 | 85.3816 | 15.57 | 10.12 | 6 | HAUL ROAD | 11.1192 | 5388
45645 | 0.8363 | 21.9309 | 85.3815 | 156.12 | 0 | 6 | HAUL ROAD | 24.5146 | 5389
45645 | 0.83632 | 21.931 | 85.3815 | 66.08 | 66.08 | 6 | HAUL ROAD | 11.12 | 5390
45645 | 0.83634 | 21.9311 | 85.3814 | 23.79 | 5.24 | 4 | S4 | 15.1671 | 5391
45645 | 0.83637 | 21.9312 | 85.3814 | 208.16 | 7.58 | 6 | HAUL ROAD | 11.1196 | 5392
45645 | 0.83639 | 21.9313 | 85.3813 | 68.8 | 93.32 | 4 | S5 | 15.1671 | 5393
45645 | 0.83641 | 21.9313 | 85.3812 | 101.5 | 5.24 | 4 | S5 | 10.3148 | 5394
45645 | 0.83644 | 21.9314 | 85.3812 | 208.16 | 26.31 | 6 | HAUL ROAD | 11.1196 | 5395
45645 | 0.83646 | 21.9315 | 85.3811 | 44.32 | 52.48 | 6 | HAUL ROAD | 15.1674 | 5396
45645 | 0.83648 | 21.9316 | 85.3811 | 147.92 | 0 | 6 | HAUL ROAD | 11.1192 | 5397
45645 | 0.8365 | 21.9317 | 85.381 | 1.39 | 0 | 6 | HAUL ROAD | 15.1671 | 5398
45645 | 0.83653 | 21.9318 | 85.3809 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 5399
45645 | 0.83655 | 21.9318 | 85.3808 | 0 | 0 | 6 | HAUL ROAD | 10.3148 | 5400
45645 | 0.83657 | 21.9318 | 85.3807 | 5.24 | 12.8 | 6 | HAUL ROAD | 10.3148 | 5401
45645 | 0.8366 | 21.9319 | 85.3806 | 12.8 | 1.39 | 6 | HAUL ROAD | 15.1671 | 5402
45645 | 0.83662 | 21.932 | 85.3805 | 0 | 1.39 | 6 | HAUL ROAD | 15.1671 | 5403
45645 | 0.83664 | 21.932 | 85.3804 | 5.24 | 10.12 | 6 | HAUL ROAD | 10.3148 | 5404
45645 | 0.83667 | 21.9321 | 85.3804 | 12.8 | 26.31 | 6 | HAUL ROAD | 11.1196 | 5405
45645 | 0.83669 | 21.9321 | 85.3803 | 30.73 | 44.32 | 6 | HAUL ROAD | 10.3152 | 5406
45645 | 0.83671 | 21.9321 | 85.3802 | 0 | 12.8 | 6 | HAUL ROAD | 10.3152 | 5407
45645 | 0.83674 | 21.9321 | 85.3801 | 5.24 | 26.31 | 6 | HAUL ROAD | 10.3152 | 5408
45645 | 0.83676 | 21.9321 | 85.38 | 15.57 | 30.73 | 6 | HAUL ROAD | 10.3152 | 5409
45645 | 0.83678 | 21.932 | 85.38 | 21.12 | 7.58 | 6 | HAUL ROAD | 11.1196 | 5410
45645 | 0.83681 | 21.9319 | 85.3799 | 10.12 | 12.8 | 6 | HAUL ROAD | 15.1671 | 5411
45645 | 0.83683 | 21.9319 | 85.3798 | 5.24 | 18.36 | 6 | HAUL ROAD | 10.3152 | 5412
45645 | 0.83685 | 21.9319 | 85.3797 | 10.12 | 10.12 | 6 | HAUL ROAD | 10.3152 | 5413
45645 | 0.83688 | 21.932 | 85.3797 | 5.24 | 0 | 6 | HAUL ROAD | 11.1196 | 5414
45645 | 0.8369 | 21.932 | 85.3797 | 7.58 | 0 | 6 | HAUL ROAD | 0 | 5415
45645 | 0.83692 | 21.9321 | 85.3797 | 10.12 | 3.16 | 6 | HAUL ROAD | 11.1196 | 5416
45645 | 0.83694 | 21.9322 | 85.3797 | 41.6 | 12.8 | 6 | HAUL ROAD | 11.1196 | 5417
45645 | 0.83697 | 21.9324 | 85.3797 | 47.04 | 0 | 6 | HAUL ROAD | 22.239 | 5418
45645 | 0.83699 | 21.9325 | 85.3798 | 10.12 | 0 | 6 | HAUL ROAD | 15.1671 | 5419
45645 | 0.83701 | 21.9326 | 85.3798 | 18.36 | 1.39 | 6 | HAUL ROAD | 11.1196 | 5420
45645 | 0.83704 | 21.9327 | 85.3799 | 3.16 | 0 | 6 | HAUL ROAD | 15.1668 | 5421
45645 | 0.83706 | 21.9328 | 85.3799 | 0 | 3.16 | 6 | HAUL ROAD | 11.1192 | 5422
45645 | 0.83708 | 21.9329 | 85.38 | 15.57 | 0 | 6 | HAUL ROAD | 15.1671 | 5423
45645 | 0.83711 | 21.933 | 85.38 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 5424
45645 | 0.83713 | 21.9331 | 85.3801 | 0 | 1.39 | 6 | HAUL ROAD | 15.1671 | 5425
45645 | 0.83715 | 21.9331 | 85.3802 | 0 | 0 | 6 | HAUL ROAD | 10.3148 | 5426
45645 | 0.83718 | 21.9332 | 85.3803 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 5427
45645 | 0.8372 | 21.9333 | 85.3804 | 10.12 | 1.39 | 6 | HAUL ROAD | 15.1671 | 5428
45645 | 0.83722 | 21.9334 | 85.3805 | 5.24 | 0 | 6 | HAUL ROAD | 15.1671 | 5429
45645 | 0.83725 | 21.9335 | 85.3806 | 1.39 | 0 | 6 | HAUL ROAD | 15.1668 | 5430
45645 | 0.83727 | 21.9336 | 85.3806 | 3.16 | 0 | 6 | HAUL ROAD | 11.1192 | 5431
45645 | 0.83729 | 21.9337 | 85.3807 | 0 | 1.39 | 6 | HAUL ROAD | 15.1671 | 5432
45645 | 0.83731 | 21.9338 | 85.3808 | 5.24 | 1.39 | 6 | HAUL ROAD | 15.1671 | 5433
45645 | 0.83734 | 21.9338 | 85.3809 | 10.12 | 0 | 6 | HAUL ROAD | 10.3148 | 5434
45645 | 0.83736 | 21.9339 | 85.381 | 0 | 1.39 | 6 | HAUL ROAD | 15.1668 | 5435
45645 | 0.83738 | 21.934 | 85.3811 | 7.58 | 0 | 6 | HAUL ROAD | 15.1671 | 5436
45645 | 0.83741 | 21.9341 | 85.3812 | 1.39 | 0 | 6 | HAUL ROAD | 15.1668 | 5437
45645 | 0.83743 | 21.9342 | 85.3813 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 5438
45645 | 0.83745 | 21.9343 | 85.3813 | 1.39 | 0 | 6 | HAUL ROAD | 11.1192 | 5439
45645 | 0.83748 | 21.9343 | 85.3814 | 1.39 | 0 | 6 | HAUL ROAD | 10.3148 | 5440
45645 | 0.8375 | 21.9344 | 85.3815 | 5.24 | 1.39 | 6 | HAUL ROAD | 15.1671 | 5441
45645 | 0.83752 | 21.9345 | 85.3816 | 10.12 | 0 | 6 | HAUL ROAD | 15.1671 | 5442
45645 | 0.83755 | 21.9346 | 85.3817 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 5443
45645 | 0.83757 | 21.9347 | 85.3817 | 7.58 | 1.39 | 6 | HAUL ROAD | 11.1192 | 5444
45645 | 0.83759 | 21.9348 | 85.3817 | 5.24 | 0 | 6 | HAUL ROAD | 11.1196 | 5445
45645 | 0.83762 | 21.9349 | 85.3817 | 7.58 | 0 | 6 | HAUL ROAD | 11.12 | 5446
45645 | 0.83764 | 21.9349 | 85.3816 | 10.12 | 0 | 6 | HAUL ROAD | 10.3152 | 5447
45645 | 0.83766 | 21.935 | 85.3815 | 0 | 0 | 6 | HAUL ROAD | 15.1671 | 5448
45645 | 0.83769 | 21.935 | 85.3814 | 0 | 1.39 | 6 | HAUL ROAD | 10.3148 | 5449
45645 | 0.83771 | 21.935 | 85.3812 | 5.24 | 0 | 6 | HAUL ROAD | 20.6292 | 5450
45645 | 0.83773 | 21.935 | 85.3811 | 0 | 0 | 6 | HAUL ROAD | 10.3148 | 5451
45645 | 0.83775 | 21.935 | 85.381 | 0 | 1.39 | 6 | HAUL ROAD | 10.3148 | 5452
45645 | 0.83778 | 21.935 | 85.3809 | 7.58 | 1.39 | 6 | HAUL ROAD | 10.3148 | 5453
45645 | 0.8378 | 21.935 | 85.3808 | 10.12 | 0 | 6 | HAUL ROAD | 10.3148 | 5454
45645 | 0.83782 | 21.935 | 85.3807 | 1.39 | 1.39 | 6 | HAUL ROAD | 10.3148 | 5455
45645 | 0.83785 | 21.935 | 85.3806 | 0 | 3.16 | 6 | HAUL ROAD | 10.3148 | 5456
45645 | 0.83787 | 21.9351 | 85.3805 | 3.16 | 1.39 | 6 | HAUL ROAD | 15.1668 | 5457
45645 | 0.83789 | 21.9352 | 85.3804 | 33.45 | 18.36 | 6 | HAUL ROAD | 15.1668 | 5458
45645 | 0.83792 | 21.9353 | 85.3804 | 38.88 | 7.58 | 6 | HAUL ROAD | 11.1192 | 5459
45645 | 0.83794 | 21.9354 | 85.3803 | 5.24 | 23.79 | 6 | HAUL ROAD | 15.1671 | 5460
45645 | 0.83796 | 21.9355 | 85.3802 | 52.48 | 21.12 | 6 | HAUL ROAD | 15.1671 | 5461
45645 | 0.83799 | 21.9356 | 85.3802 | 26.31 | 12.8 | 6 | HAUL ROAD | 11.1196 | 5462
45645 | 0.83801 | 21.9357 | 85.3802 | 38.88 | 41.6 | 6 | HAUL ROAD | 11.1196 | 5463
45645 | 0.83803 | 21.9358 | 85.3801 | 79.7 | 30.73 | 6 | HAUL ROAD | 15.1665 | 5464
45645 | 0.83806 | 21.9359 | 85.3801 | 112.41 | 10.12 | 6 | HAUL ROAD | 11.1192 | 5465
45645 | 0.83808 | 21.936 | 85.3801 | 87.87 | 0 | 6 | HAUL ROAD | 11.1196 | 5466
45645 | 0.8381 | 21.9361 | 85.3801 | 41.6 | 0 | 6 | HAUL ROAD | 11.1196 | 5467
45645 | 0.83813 | 21.9362 | 85.3802 | 5.24 | 0 | 6 | HAUL ROAD | 15.1665 | 5468
45645 | 0.83815 | 21.9363 | 85.3803 | 1.39 | 0 | 6 | HAUL ROAD | 15.1665 | 5469
45645 | 0.83817 | 21.9364 | 85.3804 | 0 | 0 | 6 | HAUL ROAD | 15.1668 | 5470
45645 | 0.83819 | 21.9365 | 85.3804 | 0 | 0 | 6 | HAUL ROAD | 11.1196 | 5471
45645 | 0.83822 | 21.9366 | 85.3805 | 0 | 1.39 | 6 | HAUL ROAD | 15.1668 | 5472
45645 | 0.83824 | 21.9367 | 85.3806 | 7.58 | 12.8 | 6 | HAUL ROAD | 15.1668 | 5473
45645 | 0.83826 | 21.9368 | 85.3806 | 26.31 | 0 | 6 | HAUL ROAD | 11.1192 | 5474
45645 | 0.83829 | 21.9369 | 85.3807 | 5.24 | 7.58 | 6 | HAUL ROAD | 15.1665 | 5475
45645 | 0.83831 | 21.937 | 85.3808 | 26.31 | 1.39 | 6 | HAUL ROAD | 15.1665 | 5476
45645 | 0.83833 | 21.937 | 85.3809 | 7.58 | 3.16 | 6 | HAUL ROAD | 10.3144 | 5477
45645 | 0.83836 | 21.9371 | 85.3809 | 10.12 | 7.58 | 6 | HAUL ROAD | 11.1196 | 5478
45645 | 0.83838 | 21.9372 | 85.381 | 18.36 | 1.39 | 6 | HAUL ROAD | 15.1668 | 5479
45645 | 0.8384 | 21.9373 | 85.3811 | 1.39 | 5.24 | 6 | HAUL ROAD | 15.1671 | 5480
45645 | 0.83843 | 21.9374 | 85.3812 | 12.8 | 5.24 | 6 | HAUL ROAD | 15.1668 | 5481
45645 | 0.83845 | 21.9375 | 85.3812 | 7.58 | 18.36 | 6 | HAUL ROAD | 11.12 | 5482
45645 | 0.83847 | 21.9376 | 85.3813 | 60.64 | 18.36 | 6 | HAUL ROAD | 15.1671 | 5483
45645 | 0.8385 | 21.9377 | 85.3814 | 30.73 | 26.31 | 6 | HAUL ROAD | 15.1668 | 5484
45645 | 0.83852 | 21.9378 | 85.3815 | 47.04 | 10.12 | 6 | HAUL ROAD | 15.1668 | 5485
45645 | 0.83854 | 21.9379 | 85.3816 | 57.92 | 0 | 6 | HAUL ROAD | 15.1665 | 5486
45645 | 0.83856 | 21.938 | 85.3817 | 38.88 | 0 | 6 | HAUL ROAD | 15.1668 | 5487
45645 | 0.83859 | 21.9381 | 85.3817 | 12.8 | 0 | 6 | HAUL ROAD | 11.1196 | 5488
45645 | 0.83861 | 21.9382 | 85.3818 | 10.12 | 7.58 | 6 | HAUL ROAD | 15.1668 | 5489
45645 | 0.83863 | 21.9383 | 85.3819 | 74.25 | 0 | 6 | HAUL ROAD | 15.1665 | 5490
45645 | 0.83866 | 21.9384 | 85.382 | 21.12 | 12.8 | 6 | HAUL ROAD | 15.1665 | 5491
45645 | 0.83868 | 21.9384 | 85.3821 | 26.31 | 1.39 | 6 | HAUL ROAD | 10.3144 | 5492
45645 | 0.8387 | 21.9385 | 85.3822 | 21.12 | 3.16 | 6 | HAUL ROAD | 15.1668 | 5493
45645 | 0.83873 | 21.9386 | 85.3823 | 15.57 | 15.57 | 6 | HAUL ROAD | 15.1671 | 5494
45645 | 0.83875 | 21.9387 | 85.3824 | 82.42 | 5.24 | 6 | HAUL ROAD | 15.1668 | 5495
45645 | 0.83877 | 21.9387 | 85.3825 | 33.45 | 12.8 | 6 | HAUL ROAD | 10.3144 | 5496
45645 | 0.8388 | 21.9388 | 85.3826 | 49.76 | 15.57 | 6 | HAUL ROAD | 15.1665 | 5497
45645 | 0.83882 | 21.9389 | 85.3827 | 44.32 | 21.12 | 6 | HAUL ROAD | 15.1668 | 5498
45645 | 0.83884 | 21.9389 | 85.3828 | 63.36 | 7.58 | 6 | HAUL ROAD | 10.3144 | 5499
45645 | 0.83887 | 21.939 | 85.3829 | 96.05 | 15.57 | 6 | HAUL ROAD | 15.1665 | 5500
45645 | 0.83889 | 21.9391 | 85.383 | 30.73 | 7.58 | 6 | HAUL ROAD | 15.1665 | 5501
45645 | 0.83891 | 21.9391 | 85.3831 | 57.92 | 7.58 | 6 | HAUL ROAD | 10.3144 | 5502
45645 | 0.83894 | 21.9392 | 85.3832 | 23.79 | 15.57 | 6 | HAUL ROAD | 15.1668 | 5503
45645 | 0.83896 | 21.9393 | 85.3833 | 47.04 | 18.36 | 6 | HAUL ROAD | 15.1668 | 5504
45645 | 0.83898 | 21.9393 | 85.3834 | 44.32 | 21.12 | 6 | HAUL ROAD | 10.3144 | 5505
45645 | 0.839 | 21.9394 | 85.3835 | 66.08 | 30.73 | 6 | HAUL ROAD | 15.1665 | 5506
45645 | 0.83903 | 21.9395 | 85.3836 | 55.2 | 26.31 | 6 | HAUL ROAD | 15.1671 | 5507
45645 | 0.83905 | 21.9395 | 85.3837 | 49.76 | 26.31 | 6 | HAUL ROAD | 10.3148 | 5508
45645 | 0.83907 | 21.9396 | 85.3838 | 60.64 | 10.12 | 6 | HAUL ROAD | 15.1668 | 5509
45645 | 0.8391 | 21.9396 | 85.3839 | 0 | 1.39 | 6 | HAUL ROAD | 10.3144 | 5510
45645 | 0.83912 | 21.9395 | 85.384 | 52.48 | 0 | 6 | HAUL ROAD | 15.1668 | 5511
45645 | 0.83914 | 21.9395 | 85.3841 | 15.57 | 0 | 6 | HAUL ROAD | 10.3148 | 5512
45645 | 0.83917 | 21.9394 | 85.3842 | 7.58 | 0 | 6 | HAUL ROAD | 15.1671 | 5513
45645 | 0.83919 | 21.9394 | 85.3843 | 5.24 | 0 | 6 | HAUL ROAD | 10.3144 | 5514
45645 | 0.83921 | 21.9394 | 85.3845 | 5.24 | 7.58 | 6 | HAUL ROAD | 20.6287 | 5515
45645 | 0.83924 | 21.9393 | 85.3846 | 175.28 | 1.39 | 6 | HAUL ROAD | 15.1665 | 5516
45645 | 0.83926 | 21.9393 | 85.3847 | 82.42 | 101.5 | 6 | HAUL ROAD | 10.3144 | 5517
45645 | 0.83928 | 21.9393 | 85.3848 | 230.12 | 5.24 | 6 | HAUL ROAD | 10.3144 | 5518
45645 | 0.83931 | 21.9394 | 85.3849 | 156.12 | 60.64 | 6 | HAUL ROAD | 15.1665 | 5519
45645 | 0.83933 | 21.9394 | 85.385 | 180.75 | 76.97 | 6 | HAUL ROAD | 10.3144 | 5520
45645 | 0.83935 | 21.9395 | 85.3851 | 33.45 | 12.8 | 6 | HAUL ROAD | 15.1671 | 5521
45645 | 0.83937 | 21.9396 | 85.3852 | 243.85 | 44.32 | 6 | HAUL ROAD | 15.1668 | 5522
45645 | 0.8394 | 21.9397 | 85.3853 | 93.32 | 79.7 | 6 | HAUL ROAD | 15.1668 | 5523
45645 | 0.83942 | 21.9398 | 85.3854 | 139.72 | 12.8 | 6 | HAUL ROAD | 15.1668 | 5524
45645 | 0.83944 | 21.9399 | 85.3854 | 199.93 | 23.79 | 6 | HAUL ROAD | 11.1192 | 5525
45645 | 0.83947 | 21.9399 | 85.3855 | 101.5 | 85.14 | 6 | HAUL ROAD | 10.3144 | 5526
45645 | 0.83949 | 21.94 | 85.3856 | 161.59 | 18.36 | 6 | HAUL ROAD | 15.1665 | 5527
45645 | 0.83951 | 21.94 | 85.3857 | 161.59 | 87.87 | 6 | HAUL ROAD | 10.3144 | 5528
45645 | 0.83954 | 21.9401 | 85.3858 | 153.39 | 115.14 | 6 | HAUL ROAD | 15.1665 | 5529
45645 | 0.83956 | 21.9401 | 85.3859 | 232.86 | 55.2 | 6 | HAUL ROAD | 10.3144 | 5530
45645 | 0.83958 | 21.9401 | 85.3859 | 194.45 | 123.33 | 6 | HAUL ROAD | 0 | 5531
45645 | 0.83961 | 21.9401 | 85.3859 | 191.71 | 126.06 | 6 | HAUL ROAD | 0 | 5532
45645 | 0.83963 | 21.9401 | 85.3859 | 188.97 | 126.06 | 6 | HAUL ROAD | 0 | 5533
45645 | 0.83965 | 21.9401 | 85.3859 | 188.97 | 126.06 | 6 | HAUL ROAD | 0 | 5534
45645 | 0.83968 | 21.9401 | 85.3859 | 188.97 | 126.06 | 6 | HAUL ROAD | 0 | 5535
45645 | 0.8397 | 21.9401 | 85.3859 | 191.71 | 123.33 | 6 | HAUL ROAD | 0 | 5536
45645 | 0.83972 | 21.9401 | 85.3859 | 191.71 | 126.06 | 6 | HAUL ROAD | 0 | 5537
45645 | 0.83975 | 21.9401 | 85.3859 | 188.97 | 126.06 | 6 | HAUL ROAD | 0 | 5538
45645 | 0.83977 | 21.9401 | 85.3859 | 188.97 | 123.33 | 6 | HAUL ROAD | 0 | 5539
45645 | 0.83979 | 21.9401 | 85.3859 | 188.97 | 126.06 | 6 | HAUL ROAD | 0 | 5540
45645 | 0.83981 | 21.9401 | 85.3859 | 126.06 | 3.16 | 6 | HAUL ROAD | 0 | 5541
45645 | 0.83984 | 21.9401 | 85.3859 | 142.45 | 5.24 | 6 | HAUL ROAD | 0 | 5542
45645 | 0.84241 | 21.9406 | 85.3862 | 12.8 | 30.73 | 19 | DUMPER TERMINAL PARKING | 63.6279 | 5543
45645 | 0.84243 | 21.9406 | 85.3862 | 5.24 | 161.59 | 19 | DUMPER TERMINAL PARKING | 0 | 5544
45645 | 0.84245 | 21.9406 | 85.3862 | 10.12 | 164.33 | 19 | DUMPER TERMINAL PARKING | 0 | 5545
45645 | 0.84248 | 21.9406 | 85.3862 | 12.8 | 156.12 | 19 | DUMPER TERMINAL PARKING | 0 | 5546
45645 | 0.8425 | 21.9405 | 85.3861 | 21.12 | 150.65 | 19 | DUMPER TERMINAL PARKING | 15.1668 | 5547
45645 | 0.84252 | 21.9405 | 85.3861 | 15.57 | 158.86 | 19 | DUMPER TERMINAL PARKING | 0.094935 | 5548
45645 | 0.84255 | 21.9405 | 85.3861 | 10.12 | 161.59 | 19 | DUMPER TERMINAL PARKING | 0.094935 | 5549
45645 | 0.84257 | 21.9405 | 85.3861 | 26.31 | 156.12 | 19 | DUMPER TERMINAL PARKING | 0.094935 | 5550
45645 | 0.84259 | 21.9405 | 85.3861 | 26.31 | 142.45 | 19 | DUMPER TERMINAL PARKING | 0.094935 | 5551
45645 | 0.84262 | 21.9405 | 85.3861 | 47.04 | 142.45 | 19 | DUMPER TERMINAL PARKING | 0.094935 | 5552
45645 | 0.84264 | 21.9405 | 85.386 | 44.32 | 145.18 | 6 | HAUL ROAD | 10.3148 | 5553
45645 | 0.84266 | 21.9405 | 85.386 | 38.88 | 145.18 | 6 | HAUL ROAD | 0.094935 | 5554
45645 | 0.84269 | 21.9405 | 85.386 | 38.88 | 139.72 | 6 | HAUL ROAD | 0.094935 | 5555
45645 | 0.84271 | 21.9405 | 85.386 | 47.04 | 131.52 | 6 | HAUL ROAD | 0.094935 | 5556
45645 | 0.84273 | 21.9405 | 85.3859 | 52.48 | 120.6 | 6 | HAUL ROAD | 10.3148 | 5557
45645 | 0.84275 | 21.9405 | 85.3859 | 38.88 | 123.33 | 6 | HAUL ROAD | 0.094935 | 5558
45645 | 0.84278 | 21.9405 | 85.3859 | 44.32 | 112.41 | 6 | HAUL ROAD | 0.094935 | 5559
45645 | 0.8428 | 21.9404 | 85.3859 | 47.04 | 112.41 | 6 | HAUL ROAD | 11.1196 | 5560
45645 | 0.84282 | 21.9404 | 85.3859 | 55.2 | 109.68 | 6 | HAUL ROAD | 0 | 5561
45645 | 0.84285 | 21.9404 | 85.3858 | 26.31 | 109.68 | 6 | HAUL ROAD | 10.3144 | 5562
45645 | 0.84315 | 21.9404 | 85.3858 | 0 | 30.73 | 6 | HAUL ROAD | 0 | 5563
45645 | 0.84317 | 21.9404 | 85.3858 | 26.31 | 1.39 | 6 | HAUL ROAD | 0 | 5564
45645 | 0.84319 | 21.9404 | 85.3859 | 0 | 180.75 | 6 | HAUL ROAD | 10.3144 | 5565
45645 | 0.84322 | 21.9404 | 85.3859 | 36.16 | 5.24 | 6 | HAUL ROAD | 0 | 5566
45645 | 0.84324 | 21.9403 | 85.3859 | 23.79 | 1.39 | 6 | HAUL ROAD | 11.1196 | 5567
45645 | 0.84326 | 21.9403 | 85.3859 | 23.79 | 120.6 | 6 | HAUL ROAD | 0 | 5568
45645 | 0.84329 | 21.9403 | 85.3859 | 0 | 0 | 6 | HAUL ROAD | 0 | 5569
45645 | 0.84331 | 21.9403 | 85.3859 | 18.36 | 1.39 | 6 | HAUL ROAD | 0 | 5570
45645 | 0.84333 | 21.9403 | 85.3859 | 0 | 30.73 | 6 | HAUL ROAD | 0 | 5571
45645 | 0.84336 | 21.9403 | 85.3859 | 10.12 | 12.8 | 6 | HAUL ROAD | 0 | 5572
45645 | 0.84338 | 21.9403 | 85.3859 | 1.39 | 12.8 | 6 | HAUL ROAD | 0 | 5573
45645 | 0.8434 | 21.9403 | 85.3859 | 3.16 | 30.73 | 6 | HAUL ROAD | 0 | 5574
45645 | 0.84343 | 21.9403 | 85.386 | 3.16 | 21.12 | 6 | HAUL ROAD | 10.3144 | 5575
45645 | 0.84345 | 21.9403 | 85.386 | 15.57 | 30.73 | 6 | HAUL ROAD | 0 | 5576
45645 | 0.84347 | 21.9403 | 85.386 | 15.57 | 33.45 | 6 | HAUL ROAD | 0 | 5577
45645 | 0.8435 | 21.9403 | 85.386 | 18.36 | 18.36 | 6 | HAUL ROAD | 0 | 5578
45645 | 0.84352 | 21.9403 | 85.3861 | 18.36 | 18.36 | 6 | HAUL ROAD | 10.3144 | 5579
45645 | 0.84354 | 21.9403 | 85.3861 | 21.12 | 18.36 | 6 | HAUL ROAD | 0 | 5580
45645 | 0.84356 | 21.9403 | 85.3861 | 21.12 | 41.6 | 6 | HAUL ROAD | 0 | 5581
45645 | 0.84359 | 21.9403 | 85.3861 | 18.36 | 63.36 | 6 | HAUL ROAD | 0 | 5582
45645 | 0.84361 | 21.9403 | 85.3861 | 7.58 | 57.92 | 6 | HAUL ROAD | 0 | 5583
45645 | 0.84363 | 21.9404 | 85.3862 | 15.57 | 26.31 | 19 | DUMPER TERMINAL PARKING | 15.1668 | 5584
45645 | 0.84366 | 21.9404 | 85.3862 | 10.12 | 96.05 | 19 | DUMPER TERMINAL PARKING | 0 | 5585
45645 | 0.84368 | 21.9404 | 85.3862 | 21.12 | 101.5 | 19 | DUMPER TERMINAL PARKING | 0 | 5586
45645 | 0.8437 | 21.9404 | 85.3862 | 12.8 | 47.04 | 19 | DUMPER TERMINAL PARKING | 0 | 5587
45645 | 0.84373 | 21.9404 | 85.3862 | 30.73 | 93.32 | 19 | DUMPER TERMINAL PARKING | 0 | 5588
45645 | 0.84375 | 21.9404 | 85.3863 | 30.73 | 98.77 | 19 | DUMPER TERMINAL PARKING | 10.3144 | 5589
45645 | 0.84377 | 21.9404 | 85.3863 | 33.45 | 98.77 | 19 | DUMPER TERMINAL PARKING | 0 | 5590
45645 | 0.8438 | 21.9404 | 85.3863 | 23.79 | 55.2 | 19 | DUMPER TERMINAL PARKING | 0 | 5591
45645 | 0.84382 | 21.9404 | 85.3863 | 7.58 | 85.14 | 19 | DUMPER TERMINAL PARKING | 0 | 5592
45645 | 0.84384 | 21.9404 | 85.3864 | 5.24 | 52.48 | 19 | DUMPER TERMINAL PARKING | 10.3144 | 5593
45645 | 0.84387 | 21.9404 | 85.3864 | 5.24 | 68.8 | 19 | DUMPER TERMINAL PARKING | 0 | 5594
45645 | 0.84389 | 21.9404 | 85.3864 | 21.12 | 26.31 | 19 | DUMPER TERMINAL PARKING | 0 | 5595
45645 | 0.84391 | 21.9404 | 85.3864 | 30.73 | 33.45 | 19 | DUMPER TERMINAL PARKING | 0 | 5596
45645 | 0.84394 | 21.9405 | 85.3864 | 33.45 | 7.58 | 19 | DUMPER TERMINAL PARKING | 11.1196 | 5597
45645 | 0.84396 | 21.9405 | 85.3865 | 5.24 | 36.16 | 19 | DUMPER TERMINAL PARKING | 10.3148 | 5598
45645 | 0.84398 | 21.9405 | 85.3865 | 3.16 | 49.76 | 19 | DUMPER TERMINAL PARKING | 0.094935 | 5599
45645 | 0.844 | 21.9405 | 85.3865 | 3.16 | 26.31 | 19 | DUMPER TERMINAL PARKING | 0.094935 | 5600
45645 | 0.84403 | 21.9405 | 85.3865 | 5.24 | 93.32 | 19 | DUMPER TERMINAL PARKING | 0.094935 | 5601
45645 | 0.84405 | 21.9405 | 85.3865 | 5.24 | 90.59 | 19 | DUMPER TERMINAL PARKING | 0.094935 | 5602
45645 | 0.84407 | 21.9405 | 85.3865 | 5.24 | 93.32 | 19 | DUMPER TERMINAL PARKING | 0.094935 | 5603
45645 | 0.8441 | 21.9405 | 85.3865 | 5.24 | 93.32 | 19 | DUMPER TERMINAL PARKING | 0.094935 | 5604
45645 | 0.84412 | 21.9405 | 85.3865 | 10.12 | 85.14 | 19 | DUMPER TERMINAL PARKING | 0.094935 | 5605
45645 | 0.84414 | 21.9405 | 85.3865 | 49.76 | 85.14 | 19 | DUMPER TERMINAL PARKING | 0.094935 | 5606
45645 | 0.84417 | 21.9405 | 85.3866 | 85.14 | 96.05 | 6 | HAUL ROAD | 10.3148 | 5607
45645 | 0.84419 | 21.9405 | 85.3866 | 93.32 | 96.05 | 6 | HAUL ROAD | 0.094935 | 5608
45645 | 0.84421 | 21.9406 | 85.3866 | 21.12 | 30.73 | 6 | HAUL ROAD | 11.1196 | 5609
45645 | 0.84424 | 21.9406 | 85.3866 | 23.79 | 101.5 | 6 | HAUL ROAD | 0 | 5610
45645 | 0.84426 | 21.9406 | 85.3866 | 26.31 | 109.68 | 6 | HAUL ROAD | 0 | 5611
45645 | 0.84428 | 21.9406 | 85.3866 | 41.6 | 98.77 | 6 | HAUL ROAD | 0 | 5612
45645 | 0.84431 | 21.9406 | 85.3866 | 38.88 | 82.42 | 6 | HAUL ROAD | 0 | 5613
45645 | 0.84433 | 21.9406 | 85.3867 | 41.6 | 79.7 | 9 | DUMPER TERMINAL PATHWAY | 10.3144 | 5614
45645 | 0.84435 | 21.9406 | 85.3867 | 74.25 | 93.32 | 9 | DUMPER TERMINAL PATHWAY | 0 | 5615
45645 | 0.84437 | 21.9407 | 85.3867 | 210.9 | 82.42 | 6 | HAUL ROAD | 11.1192 | 5616
45645 | 0.8444 | 21.9407 | 85.3867 | 356.85 | 30.73 | 6 | HAUL ROAD | 0 | 5617
45645 | 0.84442 | 21.9407 | 85.3867 | 252.1 | 41.6 | 6 | HAUL ROAD | 0 | 5618
45645 | 0.84444 | 21.9407 | 85.3867 | 68.8 | 41.6 | 6 | HAUL ROAD | 0 | 5619
45645 | 0.84447 | 21.9407 | 85.3868 | 49.76 | 36.16 | 9 | DUMPER TERMINAL PATHWAY | 10.3144 | 5620
45645 | 0.84449 | 21.9407 | 85.3868 | 33.45 | 44.32 | 9 | DUMPER TERMINAL PATHWAY | 0 | 5621
45645 | 0.84451 | 21.9407 | 85.3868 | 47.04 | 52.48 | 9 | DUMPER TERMINAL PATHWAY | 0 | 5622
45645 | 0.84454 | 21.9408 | 85.3868 | 68.8 | 71.53 | 6 | HAUL ROAD | 11.1192 | 5623
45645 | 0.84456 | 21.9408 | 85.3868 | 147.92 | 76.97 | 6 | HAUL ROAD | 0 | 5624
45645 | 0.84458 | 21.9408 | 85.3868 | 312.67 | 93.32 | 6 | HAUL ROAD | 0 | 5625
45645 | 0.84461 | 21.9408 | 85.3869 | 348.56 | 7.58 | 9 | DUMPER TERMINAL PATHWAY | 10.3139 | 5626
45645 | 0.84463 | 21.9408 | 85.3869 | 126.06 | 10.12 | 9 | DUMPER TERMINAL PATHWAY | 0 | 5627
45645 | 0.84465 | 21.9408 | 85.3869 | 74.25 | 26.31 | 9 | DUMPER TERMINAL PATHWAY | 0 | 5628
45645 | 0.84468 | 21.9408 | 85.3869 | 63.36 | 41.6 | 9 | DUMPER TERMINAL PATHWAY | 0 | 5629
45645 | 0.8447 | 21.9408 | 85.3869 | 66.08 | 12.8 | 9 | DUMPER TERMINAL PATHWAY | 0 | 5630
45645 | 0.845 | 21.9409 | 85.3867 | 18.36 | 60.64 | 6 | HAUL ROAD | 23.4342 | 5631
45645 | 0.84502 | 21.9409 | 85.3868 | 23.79 | 18.36 | 19 | TDV PARKING | 10.3144 | 5632
45645 | 0.84505 | 21.9409 | 85.3868 | 18.36 | 18.36 | 19 | TDV PARKING | 0 | 5633
45645 | 0.84507 | 21.9409 | 85.3868 | 26.31 | 30.73 | 19 | TDV PARKING | 0 | 5634
45645 | 0.84509 | 21.9409 | 85.3868 | 18.36 | 26.31 | 19 | TDV PARKING | 0 | 5635
45645 | 0.84512 | 21.9409 | 85.3868 | 21.12 | 63.36 | 19 | TDV PARKING | 0 | 5636
45645 | 0.84514 | 21.9409 | 85.3868 | 21.12 | 68.8 | 19 | TDV PARKING | 0 | 5637
45645 | 0.84516 | 21.9409 | 85.3868 | 18.36 | 76.97 | 19 | TDV PARKING | 0 | 5638
45645 | 0.84519 | 21.9409 | 85.3869 | 21.12 | 85.14 | 6 | HAUL ROAD | 10.3144 | 5639
45645 | 0.84521 | 21.941 | 85.3869 | 15.57 | 101.5 | 19 | TDV PARKING | 11.1196 | 5640
45645 | 0.84523 | 21.941 | 85.3869 | 26.31 | 101.5 | 19 | TDV PARKING | 0 | 5641
45645 | 0.84525 | 21.941 | 85.3869 | 18.36 | 104.23 | 19 | TDV PARKING | 0 | 5642
45645 | 0.84528 | 21.941 | 85.3869 | 33.45 | 112.41 | 19 | TDV PARKING | 0 | 5643
45645 | 0.8453 | 21.941 | 85.3869 | 41.6 | 101.5 | 19 | TDV PARKING | 0 | 5644
45645 | 0.84532 | 21.941 | 85.387 | 49.76 | 87.87 | 19 | TDV PARKING | 10.3139 | 5645
45645 | 0.84535 | 21.941 | 85.387 | 38.88 | 76.97 | 19 | TDV PARKING | 0 | 5646
45645 | 0.84537 | 21.941 | 85.387 | 36.16 | 63.36 | 19 | TDV PARKING | 0 | 5647
45645 | 0.84539 | 21.941 | 85.387 | 33.45 | 68.8 | 19 | TDV PARKING | 0 | 5648
45645 | 0.84542 | 21.941 | 85.387 | 26.31 | 57.92 | 19 | TDV PARKING | 0 | 5649
45645 | 0.84544 | 21.9411 | 85.387 | 26.31 | 66.08 | 19 | TDV PARKING | 11.1192 | 5650
45645 | 0.84546 | 21.9411 | 85.3871 | 33.45 | 76.97 | 19 | TDV PARKING | 10.3144 | 5651
45645 | 0.84641 | 21.9416 | 85.3871 | 44.32 | 115.14 | 6 | HAUL ROAD | 55.5975 | 5652
45645 | 0.84644 | 21.9416 | 85.3871 | 238.36 | 55.2 | 6 | HAUL ROAD | 0 | 5653
45645 | 0.84646 | 21.9416 | 85.3871 | 142.45 | 23.79 | 6 | HAUL ROAD | 0 | 5654
45645 | 0.84648 | 21.9417 | 85.387 | 60.64 | 26.31 | 6 | HAUL ROAD | 15.1668 | 5655
45645 | 0.8465 | 21.9417 | 85.387 | 26.31 | 38.88 | 6 | HAUL ROAD | 0.094935 | 5656
45645 | 0.84653 | 21.9417 | 85.387 | 26.31 | 38.88 | 6 | HAUL ROAD | 0.094935 | 5657
45645 | 0.84655 | 21.9417 | 85.387 | 38.88 | 60.64 | 6 | HAUL ROAD | 0.094935 | 5658
45645 | 0.84657 | 21.9417 | 85.387 | 33.45 | 38.88 | 6 | HAUL ROAD | 0.094935 | 5659
45645 | 0.8466 | 21.9417 | 85.387 | 126.06 | 52.48 | 6 | HAUL ROAD | 0.094935 | 5660
45645 | 0.84662 | 21.9418 | 85.387 | 93.32 | 156.12 | 20 | STORE AREA | 11.1196 | 5661
45645 | 0.84664 | 21.9418 | 85.387 | 55.2 | 63.36 | 20 | STORE AREA | 0 | 5662
45645 | 0.84667 | 21.9418 | 85.3869 | 26.31 | 41.6 | 6 | HAUL ROAD | 10.3139 | 5663
45645 | 0.84669 | 21.9418 | 85.3869 | 23.79 | 38.88 | 6 | HAUL ROAD | 0 | 5664
45645 | 0.84671 | 21.9418 | 85.3869 | 44.32 | 96.05 | 6 | HAUL ROAD | 0 | 5665
45645 | 0.84674 | 21.9418 | 85.3869 | 90.59 | 123.33 | 6 | HAUL ROAD | 0 | 5666
45645 | 0.84731 | 21.942 | 85.3872 | 131.52 | 60.64 | 17 | REST SHELTER | 38.1049 | 5667
45645 | 0.84734 | 21.9419 | 85.3873 | 23.79 | 93.32 | 17 | REST SHELTER | 15.1665 | 5668
45645 | 0.84736 | 21.9419 | 85.3873 | 147.92 | 161.59 | 17 | REST SHELTER | 0.094935 | 5669
45645 | 0.84738 | 21.942 | 85.3873 | 161.59 | 71.53 | 17 | REST SHELTER | 11.1196 | 5670
45645 | 0.84741 | 21.942 | 85.3873 | 249.35 | 21.12 | 17 | REST SHELTER | 0 | 5671
45645 | 0.84743 | 21.942 | 85.3872 | 164.33 | 10.12 | 17 | REST SHELTER | 10.3139 | 5672
45645 | 0.84745 | 21.942 | 85.3872 | 169.8 | 7.58 | 17 | REST SHELTER | 0 | 5673
45645 | 0.84748 | 21.942 | 85.3872 | 33.45 | 5.24 | 17 | REST SHELTER | 0 | 5674
45645 | 0.8475 | 21.9421 | 85.3872 | 3.16 | 5.24 | 17 | REST SHELTER | 11.12 | 5675
45645 | 0.84752 | 21.9421 | 85.3873 | 1.39 | 5.24 | 17 | REST SHELTER | 10.3144 | 5676
45645 | 0.84755 | 21.9421 | 85.3873 | 1.39 | 1.39 | 17 | REST SHELTER | 0.094935 | 5677
45645 | 0.84757 | 21.9421 | 85.3873 | 3.16 | 44.32 | 17 | REST SHELTER | 0.094935 | 5678
45645 | 0.84759 | 21.9421 | 85.3873 | 30.73 | 63.36 | 17 | REST SHELTER | 0.094935 | 5679
45645 | 0.84762 | 21.9421 | 85.3873 | 126.06 | 112.41 | 17 | REST SHELTER | 0.094935 | 5680
45645 | 0.84764 | 21.9421 | 85.3873 | 104.23 | 18.36 | 17 | REST SHELTER | 0.094935 | 5681
45645 | 0.84766 | 21.9421 | 85.3873 | 60.64 | 47.04 | 17 | REST SHELTER | 0.094935 | 5682
45645 | 0.84769 | 21.9421 | 85.3873 | 60.64 | 18.36 | 17 | REST SHELTER | 0.094935 | 5683
45645 | 0.84771 | 21.9421 | 85.3873 | 30.73 | 60.64 | 17 | REST SHELTER | 0.094935 | 5684
45645 | 0.84773 | 21.9421 | 85.3873 | 194.45 | 52.48 | 17 | REST SHELTER | 0.094935 | 5685
45645 | 0.84775 | 21.9421 | 85.3873 | 47.04 | 26.31 | 17 | REST SHELTER | 0.094935 | 5686
45645 | 0.84778 | 21.9421 | 85.3873 | 161.59 | 142.45 | 17 | REST SHELTER | 0.094935 | 5687
45645 | 0.8478 | 21.9421 | 85.3873 | 274.1 | 117.87 | 17 | REST SHELTER | 0.094935 | 5688
45645 | 0.84782 | 21.9421 | 85.3873 | 238.36 | 115.14 | 17 | REST SHELTER | 0.094935 | 5689
45645 | 0.84785 | 21.9421 | 85.3873 | 257.59 | 115.14 | 17 | REST SHELTER | 0.094935 | 5690
45645 | 0.84787 | 21.9421 | 85.3873 | 194.45 | 104.23 | 17 | REST SHELTER | 0.094935 | 5691
45645 | 0.84789 | 21.9422 | 85.3873 | 145.18 | 36.16 | 17 | REST SHELTER | 11.1196 | 5692
45645 | 0.84792 | 21.9422 | 85.3873 | 47.04 | 44.32 | 17 | REST SHELTER | 0 | 5693
45645 | 0.84794 | 21.9422 | 85.3873 | 79.7 | 36.16 | 17 | REST SHELTER | 0 | 5694
45645 | 0.84796 | 21.9422 | 85.3873 | 66.08 | 71.53 | 17 | REST SHELTER | 0 | 5695
45645 | 0.84799 | 21.9422 | 85.3872 | 117.87 | 38.88 | 17 | REST SHELTER | 10.3139 | 5696
45645 | 0.84801 | 21.9422 | 85.3872 | 60.64 | 44.32 | 17 | REST SHELTER | 0 | 5697
45645 | 0.84803 | 21.9421 | 85.3872 | 93.32 | 26.31 | 17 | REST SHELTER | 11.1196 | 5698
45645 | 0.84806 | 21.9422 | 85.3872 | 131.52 | 41.6 | 17 | REST SHELTER | 11.1196 | 5699
45645 | 0.84808 | 21.9421 | 85.3872 | 60.64 | 68.8 | 17 | REST SHELTER | 11.1196 | 5700
45645 | 0.8487 | 21.9419 | 85.3869 | 79.7 | 18.36 | 16 | FIRST AID STATION | 38.105 | 5701
45645 | 0.84873 | 21.9419 | 85.3869 | 101.5 | 87.87 | 16 | FIRST AID STATION | 0.094935 | 5702
45645 | 0.84875 | 21.9419 | 85.3869 | 104.23 | 90.59 | 16 | FIRST AID STATION | 0.094935 | 5703
45645 | 0.84877 | 21.9419 | 85.3869 | 126.06 | 74.25 | 16 | FIRST AID STATION | 0.094935 | 5704
45645 | 0.8488 | 21.9419 | 85.3869 | 115.14 | 106.96 | 16 | FIRST AID STATION | 0.094935 | 5705
45645 | 0.84882 | 21.9419 | 85.3869 | 106.96 | 98.77 | 16 | FIRST AID STATION | 0.094935 | 5706
45645 | 0.84884 | 21.9419 | 85.3869 | 150.65 | 126.06 | 16 | FIRST AID STATION | 0.094935 | 5707
45645 | 0.84887 | 21.9419 | 85.3869 | 221.88 | 76.97 | 16 | FIRST AID STATION | 0.094935 | 5708
45645 | 0.84889 | 21.9419 | 85.3869 | 172.54 | 49.76 | 16 | FIRST AID STATION | 0.094935 | 5709
45645 | 0.84891 | 21.9419 | 85.3869 | 147.92 | 55.2 | 16 | FIRST AID STATION | 0.094935 | 5710
45645 | 0.84894 | 21.9419 | 85.3869 | 227.37 | 60.64 | 16 | FIRST AID STATION | 0.094935 | 5711
45645 | 0.84896 | 21.9419 | 85.3869 | 150.65 | 44.32 | 16 | FIRST AID STATION | 0.094935 | 5712
45645 | 0.84898 | 21.9419 | 85.3869 | 93.32 | 26.31 | 16 | FIRST AID STATION | 0.094935 | 5713
45645 | 0.84924 | 21.942 | 85.3869 | 18.36 | 26.31 | 6 | HAUL ROAD | 11.1196 | 5714
45645 | 0.84926 | 21.942 | 85.3869 | 26.31 | 26.31 | 6 | HAUL ROAD | 0 | 5715
45645 | 0.84928 | 21.9421 | 85.3869 | 101.5 | 115.14 | 6 | HAUL ROAD | 11.12 | 5716
45645 | 0.84931 | 21.9421 | 85.3869 | 312.67 | 7.58 | 6 | HAUL ROAD | 0.094935 | 5717
45645 | 0.84933 | 21.942 | 85.3869 | 10.12 | 12.8 | 6 | HAUL ROAD | 11.12 | 5718
45645 | 0.84944 | 21.942 | 85.3868 | 12.8 | 0 | 15.2 | MCC ROOM | 10.3139 | 5719
45645 | 0.84947 | 21.942 | 85.3868 | 36.16 | 52.48 | 15.2 | MCC ROOM | 0 | 5720
45645 | 0.84949 | 21.942 | 85.3868 | 172.54 | 63.36 | 15.2 | MCC ROOM | 0 | 5721
45645 | 0.84951 | 21.942 | 85.3868 | 93.32 | 33.45 | 15.2 | MCC ROOM | 0 | 5722
45645 | 0.84954 | 21.942 | 85.3868 | 66.08 | 47.04 | 15.2 | MCC ROOM | 0 | 5723
45645 | 0.84956 | 21.942 | 85.3868 | 82.42 | 44.32 | 15.2 | MCC ROOM | 0 | 5724
45645 | 0.84958 | 21.942 | 85.3868 | 123.33 | 76.97 | 15.2 | MCC ROOM | 0 | 5725
45645 | 0.84961 | 21.942 | 85.3868 | 145.18 | 68.8 | 15.2 | MCC ROOM | 0 | 5726
45645 | 0.84963 | 21.942 | 85.3868 | 142.45 | 36.16 | 15.2 | MCC ROOM | 0 | 5727
45645 | 0.84965 | 21.9419 | 85.3867 | 76.97 | 36.16 | 6 | HAUL ROAD | 15.1665 | 5728
45645 | 0.84968 | 21.9419 | 85.3867 | 60.64 | 26.31 | 6 | HAUL ROAD | 0.094935 | 5729
45645 | 0.8497 | 21.9419 | 85.3867 | 74.25 | 90.59 | 6 | HAUL ROAD | 0.094935 | 5730
45645 | 0.84972 | 21.9419 | 85.3867 | 145.18 | 87.87 | 6 | HAUL ROAD | 0.094935 | 5731
45645 | 0.84988 | 21.9419 | 85.3867 | 41.6 | 26.31 | 6 | HAUL ROAD | 0.094935 | 5732
45645 | 0.84991 | 21.9419 | 85.3867 | 21.12 | 26.31 | 6 | HAUL ROAD | 0.094935 | 5733
45645 | 0.84993 | 21.9419 | 85.3867 | 49.76 | 36.16 | 6 | HAUL ROAD | 0.094935 | 5734
45645 | 0.84995 | 21.9419 | 85.3867 | 76.97 | 38.88 | 6 | HAUL ROAD | 0.094935 | 5735
45645 | 0.84998 | 21.9419 | 85.3867 | 126.06 | 26.31 | 6 | HAUL ROAD | 0.094935 | 5736
45645 | 0.85 | 21.9418 | 85.3867 | 79.7 | 12.8 | 6 | HAUL ROAD | 11.1196 | 5737
45645 | 0.85002 | 21.9418 | 85.3867 | 38.88 | 21.12 | 6 | HAUL ROAD | 0 | 5738
45645 | 0.85005 | 21.9418 | 85.3867 | 49.76 | 68.8 | 6 | HAUL ROAD | 0 | 5739
45645 | 0.85007 | 21.9418 | 85.3867 | 307.16 | 98.77 | 6 | HAUL ROAD | 0 | 5740
45645 | 0.85009 | 21.9418 | 85.3866 | 199.93 | 15.57 | 6 | HAUL ROAD | 10.3139 | 5741
45645 | 0.85012 | 21.9418 | 85.3866 | 26.31 | 26.31 | 6 | HAUL ROAD | 0 | 5742
45645 | 0.85014 | 21.9418 | 85.3866 | 55.2 | 76.97 | 6 | HAUL ROAD | 0 | 5743
45645 | 0.85016 | 21.9418 | 85.3866 | 268.6 | 63.36 | 6 | HAUL ROAD | 0 | 5744
45645 | 0.85019 | 21.9418 | 85.3866 | 147.92 | 26.31 | 6 | HAUL ROAD | 0 | 5745
45645 | 0.85021 | 21.9418 | 85.3866 | 60.64 | 44.32 | 6 | HAUL ROAD | 0 | 5746
45645 | 0.85023 | 21.9418 | 85.3865 | 96.05 | 68.8 | 6 | HAUL ROAD | 10.3139 | 5747
45645 | 0.85025 | 21.9418 | 85.3865 | 186.23 | 7.58 | 6 | HAUL ROAD | 0 | 5748
45645 | 0.85028 | 21.9417 | 85.3865 | 60.64 | 7.58 | 9 | OFFICE AREA PATHWAY | 11.1196 | 5749
45645 | 0.8503 | 21.9417 | 85.3865 | 21.12 | 26.31 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5750
45645 | 0.85032 | 21.9417 | 85.3864 | 106.96 | 60.64 | 9 | OFFICE AREA PATHWAY | 10.3144 | 5751
45645 | 0.85035 | 21.9417 | 85.3864 | 172.54 | 15.57 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5752
45645 | 0.85037 | 21.9417 | 85.3864 | 47.04 | 12.8 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5753
45645 | 0.85039 | 21.9417 | 85.3864 | 36.16 | 49.76 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5754
45645 | 0.85042 | 21.9417 | 85.3864 | 232.86 | 44.32 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5755
45645 | 0.85044 | 21.9417 | 85.3864 | 145.18 | 5.24 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5756
45645 | 0.85046 | 21.9417 | 85.3863 | 36.16 | 12.8 | 9 | OFFICE AREA PATHWAY | 10.3144 | 5757
45645 | 0.85049 | 21.9417 | 85.3863 | 79.7 | 60.64 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5758
45645 | 0.85051 | 21.9417 | 85.3863 | 265.85 | 26.31 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5759
45645 | 0.85053 | 21.9417 | 85.3863 | 136.99 | 7.58 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5760
45645 | 0.85056 | 21.9417 | 85.3863 | 26.31 | 12.8 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5761
45645 | 0.85058 | 21.9417 | 85.3863 | 76.97 | 63.36 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5762
45645 | 0.8506 | 21.9417 | 85.3863 | 202.68 | 3.16 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5763
45645 | 0.85097 | 21.9417 | 85.3859 | 12.8 | 18.36 | 14 | PUMP ROOM | 41.2564 | 5764
45645 | 0.851 | 21.9417 | 85.386 | 10.12 | 10.12 | 14 | PUMP ROOM | 10.3144 | 5765
45645 | 0.85102 | 21.9417 | 85.3859 | 23.79 | 3.16 | 14 | PUMP ROOM | 10.3144 | 5766
45645 | 0.85104 | 21.9417 | 85.3859 | 57.92 | 47.04 | 14 | PUMP ROOM | 0.094935 | 5767
45645 | 0.85106 | 21.9416 | 85.3859 | 90.59 | 52.48 | 6 | HAUL ROAD | 11.1196 | 5768
45645 | 0.85109 | 21.9416 | 85.3859 | 63.36 | 60.64 | 6 | HAUL ROAD | 0 | 5769
45645 | 0.85111 | 21.9416 | 85.3859 | 44.32 | 10.12 | 6 | HAUL ROAD | 0 | 5770
45645 | 0.85113 | 21.9416 | 85.3859 | 30.73 | 3.16 | 6 | HAUL ROAD | 0 | 5771
45645 | 0.85116 | 21.9416 | 85.3858 | 26.31 | 49.76 | 6 | HAUL ROAD | 10.3144 | 5772
45645 | 0.85118 | 21.9415 | 85.3858 | 44.32 | 26.31 | 6 | HAUL ROAD | 11.1192 | 5773
45645 | 0.8512 | 21.9415 | 85.3858 | 52.48 | 41.6 | 6 | HAUL ROAD | 0 | 5774
45645 | 0.85125 | 21.9416 | 85.3858 | 7.58 | 5.24 | 6 | HAUL ROAD | 11.1192 | 5775
45645 | 0.85192 | 21.9414 | 85.3857 | 26.31 | 38.88 | 15.2 | UPS ROOM | 24.5143 | 5776
45645 | 0.85194 | 21.9414 | 85.3857 | 74.25 | 26.31 | 15.2 | UPS ROOM | 0 | 5777
45645 | 0.85197 | 21.9414 | 85.3857 | 66.08 | 3.16 | 15.2 | UPS ROOM | 0 | 5778
45645 | 0.85199 | 21.9414 | 85.3857 | 71.53 | 10.12 | 15.2 | UPS ROOM | 0 | 5779
45645 | 0.85201 | 21.9414 | 85.3857 | 90.59 | 30.73 | 15.2 | UPS ROOM | 0 | 5780
45645 | 0.85204 | 21.9414 | 85.3857 | 98.77 | 38.88 | 15.2 | UPS ROOM | 0 | 5781
45645 | 0.85206 | 21.9414 | 85.3857 | 87.87 | 12.8 | 15.2 | UPS ROOM | 0 | 5782
45645 | 0.85208 | 21.9414 | 85.3857 | 79.7 | 26.31 | 15.2 | UPS ROOM | 0 | 5783
45645 | 0.85211 | 21.9414 | 85.3857 | 76.97 | 21.12 | 15.2 | UPS ROOM | 0 | 5784
45645 | 0.85213 | 21.9413 | 85.3857 | 79.7 | 7.58 | 15.2 | UPS ROOM | 11.1196 | 5785
45645 | 0.85215 | 21.9414 | 85.3857 | 71.53 | 49.76 | 15.2 | UPS ROOM | 11.1196 | 5786
45645 | 0.85218 | 21.9414 | 85.3857 | 76.97 | 10.12 | 15.2 | UPS ROOM | 0 | 5787
45645 | 0.85241 | 21.9413 | 85.3858 | 33.45 | 21.12 | 6 | HAUL ROAD | 15.1668 | 5788
45645 | 0.85243 | 21.9413 | 85.3858 | 60.64 | 44.32 | 6 | HAUL ROAD | 0 | 5789
45645 | 0.85245 | 21.9413 | 85.3858 | 71.53 | 47.04 | 6 | HAUL ROAD | 0 | 5790
45645 | 0.85248 | 21.9413 | 85.3858 | 106.96 | 18.36 | 6 | HAUL ROAD | 0 | 5791
45645 | 0.8525 | 21.9413 | 85.3858 | 161.59 | 96.05 | 6 | HAUL ROAD | 0 | 5792
45645 | 0.85252 | 21.9413 | 85.3858 | 169.8 | 12.8 | 6 | HAUL ROAD | 0 | 5793
45645 | 0.85255 | 21.9413 | 85.3858 | 172.54 | 44.32 | 6 | HAUL ROAD | 0 | 5794
45645 | 0.85257 | 21.9413 | 85.3858 | 104.23 | 60.64 | 6 | HAUL ROAD | 0 | 5795
45645 | 0.85259 | 21.9413 | 85.3858 | 98.77 | 63.36 | 6 | HAUL ROAD | 0 | 5796
45645 | 0.85262 | 21.9413 | 85.3858 | 79.7 | 15.57 | 6 | HAUL ROAD | 0 | 5797
45645 | 0.85421 | 21.9416 | 85.3862 | 66.08 | 33.45 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 53.0553 | 5798
45645 | 0.85424 | 21.9416 | 85.3862 | 23.79 | 68.8 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5799
45645 | 0.85426 | 21.9416 | 85.3862 | 23.79 | 63.36 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5800
45645 | 0.85428 | 21.9415 | 85.3862 | 117.87 | 79.7 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 11.1192 | 5801
45645 | 0.85431 | 21.9415 | 85.3862 | 156.12 | 63.36 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5802
45645 | 0.85433 | 21.9415 | 85.3862 | 120.6 | 68.8 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5803
45645 | 0.85435 | 21.9415 | 85.3862 | 150.65 | 66.08 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5804
45645 | 0.85437 | 21.9415 | 85.3862 | 150.65 | 57.92 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5805
45645 | 0.8544 | 21.9415 | 85.3862 | 161.59 | 66.08 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5806
45645 | 0.85442 | 21.9415 | 85.3862 | 104.23 | 71.53 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5807
45645 | 0.85444 | 21.9415 | 85.3862 | 142.45 | 79.7 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5808
45645 | 0.85447 | 21.9415 | 85.3862 | 123.33 | 52.48 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5809
45645 | 0.85449 | 21.9415 | 85.3862 | 126.06 | 47.04 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5810
45645 | 0.85451 | 21.9415 | 85.3862 | 104.23 | 57.92 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5811
45645 | 0.85454 | 21.9415 | 85.3862 | 123.33 | 52.48 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5812
45645 | 0.85456 | 21.9415 | 85.3862 | 147.92 | 41.6 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5813
45645 | 0.85458 | 21.9415 | 85.3862 | 96.05 | 57.92 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5814
45645 | 0.85461 | 21.9415 | 85.3862 | 90.59 | 49.76 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5815
45645 | 0.85463 | 21.9415 | 85.3862 | 120.6 | 60.64 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5816
45645 | 0.85465 | 21.9415 | 85.3862 | 131.52 | 38.88 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5817
45645 | 0.85468 | 21.9415 | 85.3862 | 112.41 | 26.31 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5818
45645 | 0.8547 | 21.9416 | 85.3862 | 93.32 | 30.73 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 11.1192 | 5819
45645 | 0.85472 | 21.9416 | 85.3862 | 85.14 | 26.31 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5820
45645 | 0.85475 | 21.9416 | 85.3862 | 76.97 | 26.31 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5821
45645 | 0.85477 | 21.9416 | 85.3862 | 79.7 | 23.79 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5822
45645 | 0.85479 | 21.9416 | 85.3862 | 74.25 | 10.12 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5823
45645 | 0.85481 | 21.9416 | 85.3862 | 74.25 | 10.12 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5824
45645 | 0.85484 | 21.9416 | 85.3862 | 87.87 | 44.32 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5825
45645 | 0.85486 | 21.9416 | 85.3862 | 90.59 | 47.04 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5826
45645 | 0.85488 | 21.9416 | 85.3862 | 87.87 | 52.48 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5827
45645 | 0.85491 | 21.9416 | 85.3862 | 126.06 | 74.25 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5828
45645 | 0.85493 | 21.9416 | 85.3862 | 161.59 | 63.36 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5829
45645 | 0.85495 | 21.9416 | 85.3862 | 178.02 | 96.05 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5830
45645 | 0.85498 | 21.9416 | 85.3862 | 205.42 | 87.87 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5831
45645 | 0.855 | 21.9416 | 85.3862 | 202.68 | 85.14 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5832
45645 | 0.85502 | 21.9416 | 85.3862 | 183.49 | 55.2 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5833
45645 | 0.85505 | 21.9416 | 85.3862 | 197.19 | 87.87 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5834
45645 | 0.85507 | 21.9416 | 85.3862 | 188.97 | 55.2 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5835
45645 | 0.85509 | 21.9416 | 85.3862 | 188.97 | 60.64 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5836
45645 | 0.85512 | 21.9416 | 85.3862 | 183.49 | 63.36 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5837
45645 | 0.85514 | 21.9416 | 85.3862 | 180.75 | 49.76 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5838
45645 | 0.85516 | 21.9416 | 85.3862 | 197.19 | 52.48 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5839
45645 | 0.85519 | 21.9416 | 85.3862 | 194.45 | 66.08 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5840
45645 | 0.85521 | 21.9416 | 85.3862 | 183.49 | 55.2 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5841
45645 | 0.85523 | 21.9416 | 85.3862 | 186.23 | 79.7 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5842
45645 | 0.85525 | 21.9416 | 85.3862 | 180.75 | 74.25 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5843
45645 | 0.85528 | 21.9416 | 85.3863 | 186.23 | 87.87 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 10.3144 | 5844
45645 | 0.8553 | 21.9416 | 85.3863 | 183.49 | 85.14 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5845
45645 | 0.85532 | 21.9416 | 85.3863 | 183.49 | 57.92 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5846
45645 | 0.85535 | 21.9416 | 85.3863 | 194.45 | 71.53 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5847
45645 | 0.85537 | 21.9416 | 85.3863 | 202.68 | 63.36 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5848
45645 | 0.85539 | 21.9416 | 85.3863 | 186.23 | 68.8 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5849
45645 | 0.85542 | 21.9416 | 85.3863 | 194.45 | 60.64 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5850
45645 | 0.85544 | 21.9416 | 85.3863 | 194.45 | 74.25 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5851
45645 | 0.85546 | 21.9416 | 85.3864 | 180.75 | 87.87 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 10.3144 | 5852
45645 | 0.85549 | 21.9416 | 85.3864 | 199.93 | 104.23 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5853
45645 | 0.85551 | 21.9416 | 85.3864 | 188.97 | 98.77 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5854
45645 | 0.85553 | 21.9416 | 85.3864 | 243.85 | 85.14 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5855
45645 | 0.85556 | 21.9416 | 85.3864 | 282.36 | 66.08 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5856
45645 | 0.85558 | 21.9416 | 85.3865 | 309.91 | 76.97 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 10.3144 | 5857
45645 | 0.8556 | 21.9416 | 85.3865 | 276.85 | 76.97 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5858
45645 | 0.85562 | 21.9416 | 85.3865 | 249.35 | 57.92 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5859
45645 | 0.85565 | 21.9416 | 85.3865 | 172.54 | 55.2 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5860
45645 | 0.85567 | 21.9416 | 85.3865 | 180.75 | 41.6 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5861
45645 | 0.85569 | 21.9416 | 85.3865 | 178.02 | 55.2 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5862
45645 | 0.85572 | 21.9416 | 85.3865 | 158.86 | 33.45 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5863
45645 | 0.85574 | 21.9416 | 85.3866 | 158.86 | 12.8 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 10.3144 | 5864
45645 | 0.85576 | 21.9416 | 85.3866 | 23.79 | 5.24 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5865
45645 | 0.85579 | 21.9416 | 85.3866 | 36.16 | 3.16 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5866
45645 | 0.85581 | 21.9416 | 85.3866 | 15.57 | 3.16 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5867
45645 | 0.85583 | 21.9416 | 85.3866 | 26.31 | 7.58 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5868
45645 | 0.85586 | 21.9416 | 85.3866 | 21.12 | 1.39 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5869
45645 | 0.85588 | 21.9416 | 85.3866 | 7.58 | 7.58 | 18 | WORKSHOP (NEAR EQUIPMENT OFFICE) | 0 | 5870
45645 | 0.8559 | 21.9417 | 85.3866 | 21.12 | 12.8 | 9 | OFFICE AREA PATHWAY | 11.1196 | 5871
45645 | 0.85593 | 21.9417 | 85.3866 | 10.12 | 7.58 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5872
45645 | 0.85595 | 21.9417 | 85.3866 | 1.39 | 7.58 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5873
45645 | 0.85597 | 21.9417 | 85.3866 | 18.36 | 26.31 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5874
45645 | 0.856 | 21.9417 | 85.3866 | 26.31 | 21.12 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5875
45645 | 0.85602 | 21.9417 | 85.3866 | 96.05 | 30.73 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5876
45645 | 0.85604 | 21.9417 | 85.3866 | 71.53 | 57.92 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5877
45645 | 0.85609 | 21.9417 | 85.3866 | 36.16 | 18.36 | 9 | OFFICE AREA PATHWAY | 0.094935 | 5878